## Input
User input
Input | Value | Unit | Sprinklers | Yes | Yes / No | *Sprinkler pipework allowance is not directly prescribed by AS 2118.1. The tool uses an AS-informed sprinkler spacing basis and applies a project-adjustable routing factor for early-stage pipework estimation.
NCC building class | 5 |  | Sprinkler protected area, m² | 1000 | default = total protected floor area
Total building floor area, m² | 1000 | m^2 | Sprinkler hazard classification | Ordinary Hazard | Light Hazard / Ordinary Hazard / High Hazard / user-defined | Sprinkler pipe length, m
Number of storeys | 10 | storeys | Sprinkler coverage basis | Full | Full / user-defined | = N_risers × N_storeys × floor-to-floor height + k_sprinkler × protected floor area / √(sprinkler spacing area)
Effective height, m | 20 | m | Sprinkler head spacing or area per head | 12 | default from AS assumption, override allowed
Floor-to-floor height, m | 2 |  | Pipework allowance | 23980.04 | default factor, override allowed
Number of exits | 3 |  | Sprinkler head count | 83
Number of stairs | 3 |  | Actual sprinkler head count override |  | optional
Sprinkler hazard classification | Ordinary Hazard
|  |  | Hose reels | Yes | Yes / No
System | Input |  | Hose reel served area, m² | 1000 | default = total protected floor area
Sprinklers | No / Full |  | Hose reel coverage basis | ? | default AS-based coverage / user-defined
Hydrants | Yes / No |  | Pipework allowance |  | default factor / override
Hose reels | Yes / No |  | Hose reel count
Extinguishers | Yes / No |  | Hose reel count override |  | optional
Detection system | None / Type |  |  |  | `
Alarm/warning system | None / Type |  | Extinguishers | Yes | Yes / No
Emergency lighting | Yes / No |  | Fire class basis | A | A / B / C / E / F
Exit signs | Yes / No |  | Hazard level | Ordinary Hazard | Ordinary / high / special risk
|  |  | Extinguisher type |  | ABE powder / CO₂ / foam / wet chemical / water
|  |  | Special risk areas included |  | switch room, kitchen, plant, server room
Extinguisher count
|  |  | Extinguisher count override |  | optional
Initial user input |  |  | Emergency lighting | Yes / No
Secondary user input |  |  | Emergency lighting area, m² | 1000 | default = total protected floor area
From Australian Standards |  |  | Number of exits | 3 | from general input
Output |  |  | Number of stairs | 3 | from general input
Optional override |  |  | Egress corridor allowance |  | default factor / override
|  |  | Luminaire count override |  | optional
|  |  | Hydrants | Yes / No
|  |  | Hydrant served levels | 10 | all levels / selected levels
|  |  | Number of risers |  | default from stairs/storeys, override allowed
|  |  | Hydrant outlet count |  | default estimate, override allowed
|  |  | Booster included |  | Yes / No / unknown
|  |  | Pump/tank included |  | Yes / No / unknown
|  |  | Pipe length override |  | optional
|  |  | Exit signs | Yes / No
|  |  | Number of exits | 3 | from general input
|  |  | Number of direction changes |  | default factor / override
|  |  | Number of storeys | 10 | from general input
|  |  | Exit sign count | 30
|  |  | Exit sign count override |  | optional
|  |  | Alarm/warning system type |  | None / Sounders / Speakers / EWIS / Other
|  |  | Warning system type |  | sounders / speakers / EWIS
|  |  | Warning protected area, m² | 1000 | default = total protected floor area
|  |  | Device coverage basis |  | default allowance / override
|  |  | Visual alarm devices included |  | Yes / No
|  |  | Alarm device count override |  | optional
|  |  | Detection system type |  | None / Smoke / Heat / Smoke + heat / Other
|  |  | Detection protected area, m² | 1000 | default = total protected floor area
|  |  | Detector type | Smoke | Smoke / Heat / Aspirating
|  |  | Detector spacing or coverage area | 104.04 | default AS-based / override
|  |  | Number of zones |  | default by storey / override
|  |  | Manual call points included |  | Yes / No
|  |  | Detector count override |  | optional

## Database
system | component | parameter | option | default_value | unit | evidence_level | source_basis | override
sprinkler | sprinkler_head | spacing_area | Light Hazard | 21 | m²/head | B | AS 2118.1 hazard-based spacing, team-confirmed | Yes
sprinkler | sprinkler_head | spacing_area | Ordinary Hazard | 12 | m²/head | B | AS 2118.1 hazard-based spacing, team-confirmed | Yes
sprinkler | sprinkler_head | spacing_area | High Hazard | 9 | m²/head | B | AS 2118.1 hazard-based spacing, team-confirmed | Yes
sprinkler | sprinkler_head | count_rounding | default | ROUNDUP | method | C | Derived quantity formula | No
sprinkler | sprinkler_head | quantity_formula | default | ROUNDUP(sprinkler_protected_area / spacing_area, 0) | formula | C | AS2118.1 hazard-based spacing area converted to sprinkler head count | Yes
sprinkler | pump | pump_count | <25m | 0 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
sprinkler | pump | pump_count | >25m | 1 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
sprinkler | pipework | default_risers | default | 1 | no. | D | Early-stage assumption | Yes
sprinkler | pipework | pipe_routing_factor | low | 1.1 | multiplier | D | Layout assumption | Yes
sprinkler | pipework | pipe_routing_factor | medium | 1.3 | multiplier | D | Layout assumption | Yes
sprinkler | pipework | pipe_routing_factor | high | 1.6 | multiplier | D | Layout assumption | Yes
sprinkler | pipework | drop_length_per_head | default | 0 | m/head | D | Baseline excludes drops to avoid double-counting | Yes
sprinkler | pipework | vertical_riser_formula | default | risers × storeys × floor_to_floor_height | formula | C/D | Derived from building geometry | Yes
sprinkler | pipework | horizontal_pipe_formula | default | routing_factor × area / SQRT(spacing_area) | formula | C/D | Grid-based approximation from sprinkler spacing | Yes
hydrant | hydrant_riser | default_risers | default | MAX(1, number_of_fire_stairs) | formula | D | Simplified proxy based on internal hydrants commonly being located within or adjacent to fire-isolated exits/fire stairs under AS2419.1 location logic; not a direct AS quantity rule | Yes
hydrant | hydrant_outlet | quantity_formula | default | MAX(1, number_of_fire_stairs) × number_of_storeys × outlets_per_riser_per_storey | formula | C/D | Simplified riser-per-storey method using fire stairs as the default riser proxy; actual hydrant layout requires AS2419.1 coverage assessment | Yes
hydrant | hydrant_outlet | outlets_per_riser_per_storey | default | 1 | no/riser/storey | D | Simplified early-stage assumption for internal hydrant outlets; actual outlet count depends on AS2419.1 coverage and layout | Yes
hydrant | booster | booster_count | default | IF(hydrants_selected,1,0) | no | D | Typical hydrant system allowance; final booster arrangement is project-specific | Yes
hydrant | pump | pump_count | <50m | 0 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
hydrant | pump | pump_count | >50m | 1 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
hydrant | pipework | vertical_riser_formula | default | hydrant_risers × served_storeys × floor_to_floor_height | formula | C/D | Geometry-derived vertical hydrant riser allowance | Yes
hydrant | pipework | horizontal_run_factor | default | 0.5 | multiplier | D | Average horizontal run approximated as 0.5 × SQRT(floor_plate_area) where actual routing is unknown | Yes
hydrant | pipework | horizontal_pipe_formula | default | hydrant_risers × horizontal_run_factor × SQRT(floor_plate_area) | formula | D | Layout approximation for early-stage pipework estimate from booster/feed to riser zone | Yes
hydrant | pipework | total_pipe_formula | default | (hydrant_risers × served_storeys × floor_to_floor_height) + (hydrant_risers × horizontal_run_factor × SQRT(floor_plate_area)) | formula | C/D | Vertical riser allowance plus simplified horizontal feed allowance | Yes
hose_reel | hose_reel | hose_length | default | 36 | m | B/C | AS2441 system coverage basis - 36 m hose length, verify against AS2441 | Yes
hose_reel | hose_reel | spray_allowance | default | 4 | m | B/C | AS2441 system coverage basis - 4 m spray allowance, verify against AS2441 | Yes
hose_reel | hose_reel | effective_reach | default | 40 | m path reach | B/C | AS2441 system coverage basis: 36 m hose + 4 m spray | Yes
hose_reel | hose_reel | location_basis | default | within 4 m of exit | text | B/C | AS2441 location basis, verify against AS2441 | No
hose_reel | hose_reel | min_reels_per_storey | default | 1 | no/storey | D | Simplified early-stage allowance where hose reels are selected | Yes
hose_reel | hose_reel | effective_area_per_reel | default | 400 | m^2/reel | D | Estimate from: https://cccengineering.com.au/design-memos/fire-hydrant-hose-reel-requirements/ | Yes
hose_reel | hose_reel | quantity_formula | default | number_of_storeys × MAX(1, ROUNDUP(floor_area_per_storey / effective_area_per_reel, 0)) | formula | C/D | AS2441 40 m system coverage simplified to early-stage area allowance | Yes
hose_reel | pipework | default_risers | default | 1 | no | D | Early-stage assumption unless riser count is known | Yes
hose_reel | pipework | vertical_pipe_formula | default | default_risers × number_of_storeys × floor_to_floor_height | formula | C/D | Geometry-derived riser allowance | Yes
hose_reel | pipework | horizontal_run_factor | default | 0.5 | multiplier | D | Average horizontal run approximated as 0.5 × SQRT(floor_plate_area) | Yes
hose_reel | pipework | horizontal_pipe_formula | default | hose_reel_count × horizontal_run_factor × SQRT(floor_plate_area) | formula | D | Layout approximation for early-stage pipework estimate | Yes
hose_reel | pipework | total_pipe_formula | default | (default_risers × number_of_storeys × floor_to_floor_height) + (hose_reel_count × horizontal_run_factor × SQRT(floor_plate_area)) | formula | C/D | Vertical riser allowance plus simplified horizontal distribution allowance | Yes
hose_reel | pipework | nominal_pipe_diameter | default | DN25 | pipe size | B/C | AS2441-informed secondary source - hose reel supply pipe minimum DN25, verify against AS2441 | Yes
hose_reel | cabinet | cabinet_quantity_formula | default | hose_reel_count | formula | D | Optional cabinet allowance; include only where hose reel cabinets are assumed in carbon database | Yes
extinguisher | portable_extinguisher | representative_product | Default | 6 kg powder extinguisher - 34A 233BC | type | C | EPD-IES-0019486 product family | Yes
extinguisher | portable_extinguisher | representative_rating | Default | 34A 233BC | rating | C | EPD-IES-0019486 product identification | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class A ¦ No fixed suppression ¦ 34A representative product | 675 | m2/extinguisher | B | AS2444 Table 4.1 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class A ¦ Fixed suppression ¦ 34A representative product | 1000 | m2/extinguisher | B | AS2444 Table 4.1 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | class_A_quantity_formula | default | number_of_storeys × ROUNDUP(floor_area / class_A_max_floor_area_per_extinguisher, 0) | formula | C | AS2444 Table 4.1 area basis applied floor-by-floor | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Light ¦ No fixed suppression ¦ 233B representative product | 80 | m2/extinguisher | B | AS2444 Table 4.2 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Light ¦ Fixed suppression ¦ 233B representative product | 150 | m2/extinguisher | B | AS2444 Table 4.3 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Ordinary ¦ No fixed suppression ¦ 233B representative product | 150 | m2/extinguisher | B | AS2444 Table 4.2 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Ordinary ¦ Fixed suppression ¦ 233B representative product | 300 | m2/extinguisher | B | AS2444 Table 4.3 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ High ¦ No fixed suppression ¦ 233B representative product | 300 | m2/extinguisher | B | AS2444 Table 4.2 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ High ¦ Fixed suppression ¦ 233B representative product | 300 | m2/extinguisher | B | AS2444 Table 4.3 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | class_B_quantity_formula | default | ROUNDUP(class_B_risk_area / class_B_max_floor_area_per_extinguisher, 0) | formula | C | AS2444 Table 4.2 and Table 4.3 area basis | Yes
extinguisher | portable_extinguisher | total_quantity_formula | default | class_A_extinguisher_quantity + class_B_extinguisher_quantity | formula | C | Simplified estimator aggregation | Yes
detection | smoke_detector | coverage_area | Smoke detectors | 104.04 | m2/detector | B | AS1670.1 detector spacing basis; 10.2 m × 10.2 m coverage area used for simplified estimator | Yes
detection | heat_detector | coverage_area | Heat detectors | 51.84 | m2/detector | B | AS1670.1 detector spacing basis; 7.2 m × 7.2 m coverage area used for simplified estimator | Yes
detection | aspirating_detection | coverage_area | Aspirating detection | 2000 | m2/system | D | Simplified early-stage allowance; aspirating detection layout depends on pipe network design and sampling points | Yes
detection | detection_device | quantity_formula | Smoke detectors | ROUNDUP(detection_protected_area / 104.04, 0) | formula | C | AS1670.1 spacing basis converted to area-based quantity estimate | Yes
detection | detection_device | quantity_formula | Heat detectors | ROUNDUP(detection_protected_area / 51.84, 0) | formula | C | AS1670.1 spacing basis converted to area-based quantity estimate | Yes
detection | detection_device | quantity_formula | Aspirating detection | ROUNDUP(detection_protected_area / 2000, 0) | formula | D | Simplified early-stage allowance; actual aspirating detection design requires specialist layout | Yes
detection | fire_indicator_panel | count_formula | default | IF(detection_selected, 1, 0) | no | C/D | Typical system-level allowance; most detection systems require a central indicating/control panel | Yes
detection | manual_call_point | count_formula | default | number_of_storeys × MAX(1, number_of_exits_per_storey) | no | C/D | Simplified allowance based on one manual call point per exit route per storey; actual placement requires AS1670.1 layout assessment | Yes
alarm_warning | sounder | coverage_area | Sounders | 250 | m2/device | D | Simplified audibility proxy; AS1670.4 is performance/design based and does not provide a simple m2/device estimator | Yes
alarm_warning | speaker | coverage_area | Speakers / EWIS | 200 | m2/device | D | Simplified speech/warning coverage proxy; actual speaker quantity depends on acoustic design and intelligibility requirements | Yes
alarm_warning | strobe | coverage_area | Visual alarm devices | 250 | m2/device | D | Simplified visual alarm proxy; actual requirement depends on occupancy, accessibility and layout | Yes
alarm_warning | warning_device | quantity_formula | Sounders | ROUNDUP(warning_protected_area / 250, 0) | formula | D | Area-based proxy for early-stage estimator; actual compliance requires AS1670.4 acoustic performance assessment | Yes
alarm_warning | warning_device | quantity_formula | Speakers / EWIS | ROUNDUP(warning_protected_area / 200, 0) | formula | D | Area-based proxy for early-stage estimator; actual compliance requires AS1670.4 acoustic and intelligibility assessment | Yes
alarm_warning | visual_alarm_device | quantity_formula | Visual alarm devices | ROUNDUP(warning_protected_area / 250, 0) | formula | D | Optional area-based proxy where visual alarms are selected | Yes
alarm_warning | control_panel | count_formula | default | IF(alarm_warning_selected, 1, 0) | no | C/D | Typical system-level allowance for alarm/warning control equipment | Yes
emergency_lighting | emergency_luminaire | effective_area_per_luminaire | default | 100 | m2/luminaire | D | Simplified emergency lighting density proxy; AS/NZS2293.1 is photometric/layout based rather than m2/luminaire based | Yes
emergency_lighting | emergency_luminaire | quantity_formula | default | number_of_storeys × MAX(1, ROUNDUP((total_protected_floor_area / number_of_storeys) / effective_area_per_luminaire, 0)) | formula | D | Area-based proxy for early-stage estimator; actual compliance requires AS/NZS2293.1 emergency lighting layout and photometric assessment | Yes
emergency_lighting | stair_luminaire | luminaires_per_stair_per_storey | default | 1 | no/stair/storey | D | Simplified allowance for emergency lighting to stairs; actual layout depends on stair geometry and luminaire spacing | Yes
emergency_lighting | stair_luminaire | quantity_formula | default | number_of_stairs × number_of_storeys × luminaires_per_stair_per_storey | formula | D | Simplified stair lighting allowance for early-stage carbon estimation | Yes
emergency_lighting | total_luminaire | total_quantity_formula | default | emergency_luminaire_count + stair_luminaire_count | formula | D | Aggregated early-stage emergency luminaire estimate | Yes
exit_signs | exit_sign | signs_per_exit | default | 1 | no/exit | C/D | Simplified allowance based on illuminated exit signage at required exits; actual sign placement requires AS/NZS2293.1 layout assessment | Yes
exit_signs | exit_sign | exit_sign_quantity_formula | default | number_of_storeys × number_of_exits_per_storey × signs_per_exit | formula | C/D | Required-exit based estimate; actual compliance requires exit path and sign visibility assessment under AS/NZS2293.1 | Yes
exit_signs | directional_sign | directional_sign_area_allowance | default | 500 | m2/directional sign | D | Simplified wayfinding proxy where exit path direction changes are unknown | Yes
exit_signs | directional_sign | directional_sign_quantity_formula | default | number_of_storeys × ROUNDUP((total_protected_floor_area / number_of_storeys) / directional_sign_area_allowance, 0) | formula | D | Area-based proxy for directional signs where detailed egress path layout is unavailable | Yes
exit_signs | total_exit_sign | total_quantity_formula | default | exit_sign_count + directional_sign_count | formula | D | Aggregated early-stage exit signage estimate | Yes
Exhaust systems | Smoke_exhaust_fan | Fans_per_floor | Adjoined by class 2, 3, 9 building | number_of_storeys x 3 | formula
Exhaust systems | Smoke_exhaust_fan | Fans_per_floor | Not adjoined by class 2, 3 or 9 | number_of_storeys x 2