## ui_structure
Category | Category Name | System | Apparatus | Product Type | ID_Linked_to_EC_Database | Archetype | Disclaimer | Info | Modes | Allow Multiple Rows | Units | Parent | Linked Mode | Formula System | Formula Component | Formula Parameters | Counted Apparatus | Requires FRL
1 | Means of Detection | Fire Detection and Alarm System | Smoke Detectors | point-type smoke detector, point-type smoke detector with sounder | Smoke Detector | Input |  | AS1670.1 | Total Quantity,Grid Spacing,Coverage Area |  | units |  |  | detection | smoke_detector | quantity_formula
1 | Means of Detection | Fire Detection and Alarm System | Heat Detectors | heat detector, heat detector with sounder | Heat Detector | Input |  | AS1670.1 | Total Quantity,Grid Spacing,Coverage Area |  | units |  |  | detection | heat_detector | quantity_formula
1 | Means of Detection | Fire Detection and Alarm System | Manual Call Points |  | Manual Call Point | Input |  |  |  |  | units
1 | Means of Detection | Fire Detection and Alarm System | Fire Indicator Panels |  | Fire Indicator Panel | Input |  |  |  |  | units
1 | Means of Detection | Fire Detection and Alarm System | Input/Output Module |  | Input/Output Module | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | End-of-Line Device |  | End-of-Line Device | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Fire Detection Cabling |  | Fire Detection Cabling | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Mimic Panel |  | Mimic Panel | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Graphic Display Panel |  | Graphic Display Panel | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detectors |  | Aspirating Unit | Input |  |  | Total Quantity,Grid Spacing,Coverage Area, |  | units |  |  | detection | aspirating_detection | quantity_formula
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detector Pipework |  | Sampling Pipework | Input |  |  |  |  | kg
1 | Means of Detection | Special Detection System | CO Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Flame Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Combination CO/Flame Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Lithium-Ion Battery Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | EWIS Panels |  | EWIS panel | Input |  |  |  |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Speakers | Standard Speaker, Horn Speaker | Speaker | Input |  | "Speaker spacing is generally determined by the selected manufacturer's requirements and may vary depending on the speaker type and ceiling height. For preliminary planning purposes, the spacing between adjacent speakers has been estimated at approximately two times the ceiling height or spaced as 7m X 7m, subject to confirmation against the selected manufacturer's design criteria and acoustic performance requirements. It is dependent on room area not the whole building area, each room would require a speaker at least. 250 sqm / speaker is too large. | Total Quantity,Grid Spacing,Coverage Area |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Warden Intercom Point |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | Visual Warning System | Visual Alarm Devices |  | Visual alarm device | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
2 | Means of Warning | Audible Warning System | Sounders |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. | Spacing is dependent on manufacturer's requirement, normally spaced as 10m X 10m. |  |  | units
2 | Means of Warning | Fire Alarm Cabling | EWIS Fire-Rated Cabling |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
3 | Means of Egress | Emergency Lighting System | Emergency Luminaires |  | Emergency Luminaire | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
3 | Means of Egress | Exit Signage System | Exit Signs | Illuminated Exit Sign, Directional Exit Sign | Illuminated Exit Sign | Input |  |  | Total Quantity |  | units
4 | Means of First Aid Fire-Fighting | Portable Extinguisher System | Extinguishers | CO₂, Dry Powder, Water, Wet Chemical | Extinguishers | Input |  | AS2444 |  |  | units
4 | Means of First Aid Fire-Fighting | Fire Blanket | Fire Blanket | 0.9m X 0.9m, 1.8m X 1.8m | Fire Blanket | Unavailable |  | AS 2444 - 2001
4 | Means of First Aid Fire-Fighting | Fire Hose Reels | Hose Reel Assembly | 19 mm hose reel, 25 mm hose reel | Hose reel , Cabinet, Fire Hose Reel, Hose reel valve | Input |  |  |  |  | reels
4 | Means of First Aid Fire-Fighting | Fire Hose Reels | Hose Reel Pipework | Copper, Galvanised mild steel, HDPE | Pipework | Unavailable |  |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Plasterboard Wall Assembly |  | Fire Resistant Plasterboard | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Speed Panel Wall Assembly |  | Speed Panel | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Masonry Wall Assembly |  | Masonry | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Concrete Wall Assembly |  | Concrete | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors |  | Fire Door | Input |  |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors (Steel with Glazing) |  | Fire Door(Steel with Glazing) | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Resistant Glazing |  | Glass Glazing | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Smoke Doors |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | doors
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Shutters |  | Fire Shutter | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Curtains |  | Fire Curtain | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Duct Penetration Protection | Fusible-Link Fire Damper |  | Fusible link damper | Input | Ensure the selected product's size is suitable for the actual duct size being protected. |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire Batts |  | Mastic Fire batt | Input |  |  |  |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Collars |  | Fire collar | Input | Ensure the selected product's size is suitable for the actual pipe diameter being protected. |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Joint Seals |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Pipe Wraps |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Mastic |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Intumescent Coating |  | Intumescent coating | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Spray-Applied Fire Protection |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m2
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Heads | Exposed, Concealed, Semi-Recessed, Sidewall | Sprinkler Heads | Input |  | AS 2118.1 hazard-based spacing | Total Quantity,Grid Spacing,Coverage Area | Y | units
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Pipework | galvanised mild steel | Sprinkler Pipework | Input |  | Refer to AS 2118.1:2017 Clause 7.10 for sprinkler pipework material requirements | Total Quantity,Formula |  | m
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Valves |  | Sprinkler Valves | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Sprinkler Heads |  | Pre-Action Sprinkler Heads | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Dry Pipework | hot-dip galvanised medium steel tube | Dry Pipework | Unavailable | Future Implmentation: Embodied carbon data is not currently available. | Refer to AS 2118.1:2017 Clause 7.10 for sprinkler pipework material requirements |  |  | m
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Valve Assembly |  | Pre-Action Valve Assembly | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Nitrogen Generator |  | Nitrogen Generator | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
6 | Means of Suppression | Fire Water Supply Equipment | Main Fire Pump Set | Electric-Driven, Diesel-Driven | Main Fire Pump Set | Input |  |  |  |  | kg
6 | Means of Suppression | Fire Water Supply Equipment | Jockey Pump Set |  | Jockey Pump Set | Input | Future Implmentation: Embodied carbon data is not currently available. This apparatus is excluded from the current estimate.
6 | Means of Suppression | Fire Water Supply Equipment | Water Tank | Reinforced Concrete, Stainless Steel | Water Tank | Unavailable | Future Implmentation: Embodied carbon data is not currently available. | Tank capacities vary depending on building height, building classification and system configuration.
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Exhaust Fan |  | Smoke Exhaust Fan (notional - 1000mm) | Input |  |  |  |  | kg
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Subducts | Fire-Rated, Non-Fire-Rated | Smoke Subducts | Input | Ensure the selected product matches the desired duct size. |  |  |  | m2
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Motorised Smoke Dampers |  | Motorised Smoke Dampers | Input | Ensure the selected product's size is suitable for the actual duct size being protected. |  |  |  | units
8 | Means of Fire Brigade Access and Intervention | Hydrant System | Hydrants |  | Hydrants | Input
8 | Means of Fire Brigade Access and Intervention | Hydrant System | Hydrant Pipework |  | Hydrant Pipework | Input |  |  |  |  | m
9 | Fire Safety Management | Fire Safety Signage and Information | Regulatory and Operational Signs |  | Fire Safety Signage System | Input |  |  | Total Quantity | Y | units
9 | Fire Safety Management | Fire Safety Signage and Information | Evacuation Diagrams | Standard Evacuation Diagram | Evacuation Diagram System | Unavailable |  |  |  |  | systems
9 | Fire Safety Management | Fire Safety Signage and Information | Fire Equipment Identification Signs | Extinguisher, Hose Reel, Hydrant | Fire Equipment Identification Sign | Unavailable | [10 empty] | Extinguishers,Hose Reel Assembly,Hydrants,Hydrant Boosters
10 | Special Hazards | Special Hazard Systems | Data-Centre Gaseous Suppression Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Battery Energy Storage Fire Protection Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Commercial Kitchen Suppression Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Carpark Special Detection Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Atrium Fire and Smoke-Control Systems |  |  | Unavailable

## calc_rules
system | component | parameter | condition_key | condition_value | value | unit | notes
sprinkler | sprinkler_head | spacing_area | hazard_class | Light Hazard | 21 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | spacing_area | hazard_class | Ordinary Hazard | 12 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | spacing_area | hazard_class | High Hazard | 9 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / spacing_area, 0) | formula | Area / spacing, rounded up
sprinkler | pipework | default_risers | default | default | 1 | no. | Fallback only - real Risers input from Project Info takes priority
sprinkler | pipework | vertical_riser_formula | default | default | FORMULA: risers * storeys * floor_to_floor_height | formula | UNVERIFIED assumption - derived from building geometry, not a cited AS clause. Confirm before relying on it.
sprinkler | pipework | horizontal_pipe_formula | default | default | FORMULA: protected_area / SQRT(spacing_area) | formula | UNVERIFIED assumption - grid-based approximation from sprinkler spacing, not a cited AS clause. Confirm before relying on it.
hose_reel | hose_reel | effective_area_per_reel | default | default | 400 | m2/reel | Coverage-based allowance (see source reference in notes)
hose_reel | hose_reel | quantity_formula | default | default | FORMULA: storeys * MAX(1, ROUNDUP(area_per_storey / effective_area_per_reel, 0)) | formula | Per-storey coverage allowance
hose_reel | cabinet | cabinet_quantity_formula | default | default | FORMULA: hose_reel_count | formula | Definitional: cabinets always equal hose reel count
detection | smoke_detector | coverage_area | default | default | 104.04 | m2/detector | AS1670.1 10.2m x 10.2m coverage
detection | heat_detector | coverage_area | default | default | 51.84 | m2/detector | AS1670.1 7.2m x 7.2m coverage
detection | aspirating_detection | coverage_area | default | default | 2000 | m2/system | Simplified early-stage allowance - not a specific AS clause
detection | fire_indicator_panel | count_formula | default | default | FORMULA: IF(detection_selected, 1, 0) | formula | One panel per detection system
detection | manual_call_point | count_formula | default | default | FORMULA: storeys * MAX(1, exits_per_storey) | formula | One per exit route per storey
extinguisher | portable_extinguisher | quantity_formula | default | default | FORMULA: storeys * ROUNDUP((floor_area / storeys) / max_area, 0) | formula | AS2444 area basis applied floor-by-floor, using the max area for the selected (hazard, rating, suppression) combination
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | Light | 1A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | Ordinary | 2A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | High | 2A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦1A | 100 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦2A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦3A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦4A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦2A | 100 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦3A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦4A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦6A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦2A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦3A | 200 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦4A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦6A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦10A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦1A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦2A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦3A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦4A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦2A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦3A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦4A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦6A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦2A | 225 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦3A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦4A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦6A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦10A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | Light | 5B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | Ordinary | 20B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | High | 40B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦5B | 15 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦10B | 45 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦20B | 80 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦20B | 80 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦30B | 115 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦40B | 150 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦40B | 150 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦60B | 225 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦80B | 300 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦5B | 80 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦10B | 115 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦20B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦20B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦30B | 225 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦40B | 300 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦40B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦60B | 225 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦80B | 300 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦5B | 2 to 3 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦10B | 2 to 4 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦20B | 2 to 5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦20B | 3 to 5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦30B | 3 to 7.5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦40B | 3 to 10 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦40B | 4 to 10 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦60B | 4 to 12.5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦80B | 4 to 15 | m | AS2444 Table 4.2
hydrant | hydrant_riser | min_risers | default | default | 1 | no. | Minimum riser allowance
hydrant | hydrant_outlet | outlets_per_riser_per_storey | default | default | 1 | no/riser/storey | PROXY - simplified AS2419.1 proxy, not a direct AS quantity rule
hydrant | hydrant_outlet | quantity_formula | default | default | FORMULA: risers * storeys * outlets_per_riser_per_storey | formula | Riser-per-storey method - PROXY, verify against AS2419.1 layout
hydrant | booster | booster_count | default | default | 1 | no. | Typical hydrant allowance if selected
emergency_lighting | emergency_luminaire | effective_area_per_luminaire | default | default | 100 | m2/luminaire | Density proxy - AS/NZS2293.1 is photometric-based, not m2/luminaire based
emergency_lighting | emergency_luminaire | quantity_formula | default | default | FORMULA: storeys * MAX(1, ROUNDUP((protected_area / storeys) / effective_area_per_luminaire, 0)) | formula | Area-based proxy
emergency_lighting | stair_luminaire | luminaires_per_stair_per_storey | default | default | 1 | no/stair/storey | Simplified stair allowance
emergency_lighting | stair_luminaire | quantity_formula | default | default | FORMULA: stairs * storeys * luminaires_per_stair_per_storey | formula | Stair lighting allowance
emergency_lighting | emergency_luminaire | egress_corridor_factor | default | default | 10 | multiplier | Default egress corridor allowance - user override recommended
exit_signs | exit_sign | signs_per_exit | default | default | 1 | no/exit | Simplified allowance
exit_signs | exit_sign | quantity_formula | default | default | FORMULA: storeys * exits_per_storey * signs_per_exit | formula | Required-exit based estimate
exit_signs | directional_sign | area_allowance | default | default | 500 | m2/sign | PROXY - wayfinding proxy where path layout is unavailable
exit_signs | directional_sign | quantity_formula | default | default | FORMULA: storeys * ROUNDUP((protected_area / storeys) / area_allowance, 0) | formula | Area-based proxy - low confidence
alarm_warning | sounder | coverage_area | default | default | 250 | m2/device | PROXY - AS1670.4 is performance-based, no simple m2/device estimator exists
alarm_warning | speaker | coverage_area | default | default | 200 | m2/device | PROXY - actual quantity depends on acoustic design
alarm_warning | strobe | coverage_area | default | default | 250 | m2/device | PROXY - actual requirement depends on occupancy/accessibility
alarm_warning | warning_device | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area-based proxy - low confidence, verify against AS1670.4
alarm_warning | control_panel | count_formula | default | default | FORMULA: IF(alarm_warning_selected, 1, 0) | formula | One panel per system
detection | smoke_detector | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area / coverage, rounded up
detection | heat_detector | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area / coverage, rounded up
detection | aspirating_detection | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area / coverage, rounded up

## frl_reference
Apparatus | Product Type | FRL (min) | Thickness (mm) | Layers | Density (kg/m3)
Concrete | 20MPa | 30 | 60 |  | 2400
Concrete | 20MPa | 60 | 80 |  | 2400
Concrete | 20MPa | 90 | 100 |  | 2400
Concrete | 20MPa | 120 | 120 |  | 2400
Concrete | 20MPa | 180 | 150 |  | 2400
Concrete | 20MPa | 240 | 175 |  | 2400
Masonry |  | 30 | 60 |  | 1900
Masonry |  | 60 | 90 |  | 1900
Masonry |  | 90 | 110 |  | 1900
Masonry |  | 120 | 130 |  | 1900
Masonry |  | 180 | 160 |  | 1900
Masonry |  | 240 | 180 |  | 1900
Speed Panel |  | 60 | 51 |  | 600
Speed Panel |  | 90 | 64 |  | 600
Speed Panel |  | 120 | 78 |  | 600
Fire Resistant Plasterboard | 13 | 30 |  | 2
Fire Resistant Plasterboard | 16 | 60 |  | 1
Fire Resistant Plasterboard | 13 | 90 |  | 2
Fire Resistant Plasterboard | 16 | 120 |  | 2