## ui_structure
Category | Category Name | System | Apparatus | Product Type | ID_Linked_to_EC_Database | Archetype | Disclaimer | Info | Modes | Allow Multiple Rows | Units | Parent | Linked Mode | Formula System | Formula Component | Formula Parameters | Counted Apparatus | Requires FRL
1 | Means of Detection | Fire Detection and Alarm System | Smoke Detectors | point-type smoke detector, point-type smoke detector with sounder | Smoke Detector | Input |  | AS1670.1 | Total Quantity,Grid Spacing,Coverage Area |  | units |  |  | detection | smoke_detector | quantity_formula
1 | Means of Detection | Fire Detection and Alarm System | Heat Detectors | heat detector, heat detector with sounder | Heat Detector | Input |  | AS1670.1 | Total Quantity,Grid Spacing,Coverage Area |  | units |  |  | detection | heat_detector | quantity_formula
1 | Means of Detection | Fire Detection and Alarm System | Manual Call Points |  | Manual call point | Input |  |  |  |  | units
1 | Means of Detection | Fire Detection and Alarm System | Fire Indicator Panels |  | Fire Indicator Panel | Input |  |  |  |  | units
1 | Means of Detection | Fire Detection and Alarm System | Input/Output Module |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | End-of-Line Device |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Fire Detection Cabling |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Mimic Panel |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Graphic Display Panel |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detectors |  | Aspirating Unit | Input |  |  | Total Quantity,Grid Spacing,Coverage Area,Formula |  | units |  |  | detection | aspirating_detection | quantity_formula
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detector Pipework |  | Sampling Pipework | Input |  |  |  |  | kg
1 | Means of Detection | Special Detection System | CO Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Flame Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Combination CO/Flame Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Lithium-Ion Battery Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | EWIS Panels |  | EWIS panel | Input |  |  |  |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Speakers | Standard Speaker, Horn Speaker | Speaker | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Warden Intercom Point |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | Visual Warning System | Visual Alarm Devices |  | Visual alarm device | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
2 | Means of Warning | Audible Warning System | Sounders |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | Fire Alarm Cabling | EWIS Fire-Rated Cabling |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
3 | Means of Egress | Emergency Lighting System | Emergency Luminaires |  | Emergency Luminaire | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
3 | Means of Egress | Exit Signage System | Exit Signs | Illuminated Exit Sign, Directional Exit Sign | Illuminated Exit Sign | Input |  |  | Total Quantity |  | units
4 | Means of First Aid Fire-Fighting | Portable Extinguisher System | Extinguishers | CO₂, Dry Powder, Water, Wet Chemical | Fire extinguishers | Input |  | AS2444 |  |  | units
4 | Means of First Aid Fire-Fighting | Fire Blanket | Fire Blanket | 0.9m X 0.9m, 1.8m X 1.8m |  | Unavailable
4 | Means of First Aid Fire-Fighting | Hose Reels | Hose Reel Assembly | 19 mm hose reel, 25 mm hose reel | Hose reel , Cabinet, Fire Hose Reel, Hose reel valve | Input |  |  |  |  | reels
4 | Means of First Aid Fire-Fighting | Hose Reels | Hose Reel Pipework | Copper, Galvanised mild steel, HDPE | Pipework | Input |  |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Plasterboard Wall Assembly |  | Fire Resistant Plasterboard | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Speed Panel Wall Assembly |  | Speed Panel | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Masonry Wall Assembly |  | Masonry | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Concrete Wall Assembly |  | Concrete | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors |  | Fire Door | Input |  |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors (Steel with Glazing) |  | Fire Door(Steel with Glazing) | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Resistant Glazing |  | Glass Glazing | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Smoke Doors |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | doors
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Shutters |  | Fire Shutter | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Curtains |  | Fire Curtain | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Duct Penetration Protection | Fusible-Link Fire Damper |  | Fusible link damper | Input | Ensure the selected product's size is suitable for the actual duct size being protected. |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire Batts |  | Mastic Fire batt | Input |  |  |  |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Collars |  | Fire collar | Input | Ensure the selected product's size is suitable for the actual pipe diameter being protected. |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Joint Seals |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Pipe Wraps |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Mastic |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Intumescent Coating |  | Intumescent coating | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Spray-Applied Fire Protection |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m2
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Heads | Exposed, Concealed, Semi-Recessed, Sidewall | Sprinkler Head | Input |  | AS 2118.1 hazard-based spacing | Total Quantity,Grid Spacing,Coverage Area | Y | units
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Pipework |  | Sprinkler Pipework | Input | The Formula option is an early-stage geometric approximation, not a cited AS clause - verify before relying on it for design. |  | Total Quantity,Formula |  | m
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Valves |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Sprinkler Heads |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Dry Pipework |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Valve Assembly |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Nitrogen Generator |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
6 | Means of Suppression | Fire Water Supply Equipment | Water Tank | Reinforced Concrete, Stainless Steel |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Fire Water Supply Equipment | Main Fire Pump Set | Electric-Driven, Diesel-Driven | Pump sets | Input |  |  |  |  | kg
6 | Means of Suppression | Fire Water Supply Equipment | Jockey Pump Set |  |  | Input | Future Implmentation: Embodied carbon data is not currently available. This apparatus is excluded from the current estimate.
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Exhaust Fan |  | Smoke Exhaust Fan (notional - 1000mm) | Input |  |  |  |  | kg
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Subducts |  | Smoke Subducts | Input | Ensure the selected product matches the desired duct size. |  |  |  | m2
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Motorised Smoke Dampers |  | Motorized Dampers | Input | Ensure the selected product's size is suitable for the actual duct size being protected. |  |  |  | units
8 | Means of Fire Brigade Access and Intervention | Hydrants | Hydrants |  | Hydrants | Input
8 | Means of Fire Brigade Access and Intervention | Hydrants | Hydrant Pipework |  | Hydrant Pipework | Input |  |  |  |  | m
8 | Means of Fire Brigade Access and Intervention | Hydrants | Hydrant Boosters |  |  | Unavailable | Typically 1 booster assembly per hydrant system - confirm against site layout and AS2419.1. |  |  |  | boosters
9 | Fire Safety Management | Fire Safety Signage and Information | Regulatory and Operational Signs | No-Storage Sign, Keep-Clear Sign, Fire-Door Sign | Fire safety signage system | Input |  |  | Total Quantity | Y | units
9 | Fire Safety Management | Fire Safety Signage and Information | Evacuation Diagrams | Standard Evacuation Diagram | Evacuation Diagram System | Unavailable |  |  |  |  | systems
9 | Fire Safety Management | Fire Safety Signage and Information | Fire Equipment Identification Signs | Extinguisher, Hose Reel, Hydrant | Fire Equipment Identification Sign | Unavailable | [10 empty] | Extinguishers,Hose Reel Assembly,Hydrants,Hydrant Boosters
10 | Special Hazards | Special Hazard Systems | Data-Centre Gaseous Suppression Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Battery Energy Storage Fire Protection Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Commercial Kitchen Suppression Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Carpark Special Detection Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Atrium Fire and Smoke-Control Systems |  |  | Unavailable

## calc_rules
system | component | parameter | condition_key | condition_value | value | unit | notes
sprinkler | sprinkler_head | spacing_area | hazard_class | Light Hazard | 21 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | spacing_area | hazard_class | Ordinary Hazard | 12 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | spacing_area | hazard_class | High Hazard | 9 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / spacing_area, 0) | formula | Area / spacing, rounded up
sprinkler | pipework | default_risers | default | default | 1 | no. | Fallback only - real Risers input from Project Info takes priority
sprinkler | pipework | vertical_riser_formula | default | default | FORMULA: risers * storeys * floor_to_floor_height | formula | UNVERIFIED assumption - derived from building geometry, not a cited AS clause. Confirm before relying on it.
sprinkler | pipework | horizontal_pipe_formula | default | default | FORMULA: protected_area / SQRT(spacing_area) | formula | UNVERIFIED assumption - grid-based approximation from sprinkler spacing, not a cited AS clause. Confirm before relying on it.
hose_reel | hose_reel | effective_area_per_reel | default | default | 400 | m2/reel | Coverage-based allowance (see source reference in notes)
hose_reel | hose_reel | quantity_formula | default | default | FORMULA: storeys * MAX(1, ROUNDUP(area_per_storey / effective_area_per_reel, 0)) | formula | Per-storey coverage allowance
hose_reel | cabinet | cabinet_quantity_formula | default | default | FORMULA: hose_reel_count | formula | Definitional: cabinets always equal hose reel count
detection | smoke_detector | coverage_area | default | default | 104.04 | m2/detector | AS1670.1 10.2m x 10.2m coverage
detection | heat_detector | coverage_area | default | default | 51.84 | m2/detector | AS1670.1 7.2m x 7.2m coverage
detection | aspirating_detection | coverage_area | default | default | 2000 | m2/system | Simplified early-stage allowance - not a specific AS clause
detection | fire_indicator_panel | count_formula | default | default | FORMULA: IF(detection_selected, 1, 0) | formula | One panel per detection system
detection | manual_call_point | count_formula | default | default | FORMULA: storeys * MAX(1, exits_per_storey) | formula | One per exit route per storey
extinguisher | portable_extinguisher | quantity_formula | default | default | FORMULA: storeys * ROUNDUP((floor_area / storeys) / max_area, 0) | formula | AS2444 area basis applied floor-by-floor, using the max area for the selected (hazard, rating, suppression) combination
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | Light | 1A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | Ordinary | 2A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | High | 2A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦1A | 100 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦2A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦3A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦4A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦2A | 100 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦3A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦4A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦6A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦2A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦3A | 200 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦4A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦6A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦10A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦1A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦2A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦3A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦4A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦2A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦3A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦4A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦6A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦2A | 225 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦3A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦4A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦6A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦10A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | Light | 5B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | Ordinary | 20B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | High | 40B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦5B | 15 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦10B | 45 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦20B | 80 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦20B | 80 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦30B | 115 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦40B | 150 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦40B | 150 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦60B | 225 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦80B | 300 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦5B | 80 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦10B | 115 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦20B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦20B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦30B | 225 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦40B | 300 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦40B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦60B | 225 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦80B | 300 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦5B | 2 to 3 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦10B | 2 to 4 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦20B | 2 to 5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦20B | 3 to 5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦30B | 3 to 7.5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦40B | 3 to 10 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦40B | 4 to 10 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦60B | 4 to 12.5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦80B | 4 to 15 | m | AS2444 Table 4.2
hydrant | hydrant_riser | min_risers | default | default | 1 | no. | Minimum riser allowance
hydrant | hydrant_outlet | outlets_per_riser_per_storey | default | default | 1 | no/riser/storey | PROXY - simplified AS2419.1 proxy, not a direct AS quantity rule
hydrant | hydrant_outlet | quantity_formula | default | default | FORMULA: risers * storeys * outlets_per_riser_per_storey | formula | Riser-per-storey method - PROXY, verify against AS2419.1 layout
hydrant | booster | booster_count | default | default | 1 | no. | Typical hydrant allowance if selected
emergency_lighting | emergency_luminaire | effective_area_per_luminaire | default | default | 100 | m2/luminaire | Density proxy - AS/NZS2293.1 is photometric-based, not m2/luminaire based
emergency_lighting | emergency_luminaire | quantity_formula | default | default | FORMULA: storeys * MAX(1, ROUNDUP((protected_area / storeys) / effective_area_per_luminaire, 0)) | formula | Area-based proxy
emergency_lighting | stair_luminaire | luminaires_per_stair_per_storey | default | default | 1 | no/stair/storey | Simplified stair allowance
emergency_lighting | stair_luminaire | quantity_formula | default | default | FORMULA: stairs * storeys * luminaires_per_stair_per_storey | formula | Stair lighting allowance
emergency_lighting | emergency_luminaire | egress_corridor_factor | default | default | 10 | multiplier | Default egress corridor allowance - user override recommended
exit_signs | exit_sign | signs_per_exit | default | default | 1 | no/exit | Simplified allowance
exit_signs | exit_sign | quantity_formula | default | default | FORMULA: storeys * exits_per_storey * signs_per_exit | formula | Required-exit based estimate
exit_signs | directional_sign | area_allowance | default | default | 500 | m2/sign | PROXY - wayfinding proxy where path layout is unavailable
exit_signs | directional_sign | quantity_formula | default | default | FORMULA: storeys * ROUNDUP((protected_area / storeys) / area_allowance, 0) | formula | Area-based proxy - low confidence
alarm_warning | sounder | coverage_area | default | default | 250 | m2/device | PROXY - AS1670.4 is performance-based, no simple m2/device estimator exists
alarm_warning | speaker | coverage_area | default | default | 200 | m2/device | PROXY - actual quantity depends on acoustic design
alarm_warning | strobe | coverage_area | default | default | 250 | m2/device | PROXY - actual requirement depends on occupancy/accessibility
alarm_warning | warning_device | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area-based proxy - low confidence, verify against AS1670.4
alarm_warning | control_panel | count_formula | default | default | FORMULA: IF(alarm_warning_selected, 1, 0) | formula | One panel per system
detection | smoke_detector | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area / coverage, rounded up
detection | heat_detector | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area / coverage, rounded up
detection | aspirating_detection | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area / coverage, rounded up

## frl_reference
Apparatus | Product Type | FRL (min) | Thickness (mm) | Layers | Density (kg/m3)
Concrete |  | 30 | 60 |  | 2400
Concrete |  | 60 | 80 |  | 2400
Concrete |  | 90 | 100 |  | 2400
Concrete |  | 120 | 120 |  | 2400
Concrete |  | 180 | 150 |  | 2400
Concrete |  | 240 | 175 |  | 2400
Masonry |  | 30 | 60 |  | 1900
Masonry |  | 60 | 90 |  | 1900
Masonry |  | 90 | 110 |  | 1900
Masonry |  | 120 | 130 |  | 1900
Masonry |  | 180 | 160 |  | 1900
Masonry |  | 240 | 180 |  | 1900
Speed Panel |  | 60 | 51 |  | 600
Speed Panel |  | 90 | 64 |  | 600
Speed Panel |  | 120 | 78 |  | 600
Fire Resistant Plasterboard | 13mm | 30 |  | 2
Fire Resistant Plasterboard | 16mm | 60 |  | 1
Fire Resistant Plasterboard | 13mm | 90 |  | 2
Fire Resistant Plasterboard | 16mm | 120 |  | 2

## Tracker
Category | Category Name | System | Apparatus | Product Type | ID_Linked_to_EC_Database | Archetype | Disclaimer | Reference | Modes | Allow Multiple Rows | Units | Parent | Linked Mode | Formula System | Formula Component | Formula Parameters | Counted Apparatus | Requires FRL
1 | Means of Detection | Fire Detection and Alarm System | Smoke Detectors | point-type smoke detector, point-type smoke detector with sounder | Smoke Detector | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units |  |  | detection | smoke_detector | quantity_formula
1 | Means of Detection | Fire Detection and Alarm System | Heat Detectors | heat detector, heat detector with sounder | Heat Detector | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units |  |  | detection | heat_detector | quantity_formula
1 | Means of Detection | Fire Detection and Alarm System | Manual Call Points |  | Manual call point | Input |  |  |  |  | units
1 | Means of Detection | Fire Detection and Alarm System | Fire Indicator Panels |  | Fire Indicator Panel | Input |  |  |  |  | units
1 | Means of Detection | Fire Detection and Alarm System | Input/Output Module |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | End-of-Line Device |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Fire Detection Cabling |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Mimic Panel |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Graphic Display Panel |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detectors |  | Aspirating Unit | Input |  |  | Total Quantity,Grid Spacing,Coverage Area,Formula |  | units |  |  | detection | aspirating_detection | quantity_formula
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detector Pipework |  | Sampling Pipework | Input |  |  |  |  | kg
1 | Means of Detection | Special Detection System | CO Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Flame Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Combination CO/Flame Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
1 | Means of Detection | Special Detection System | Lithium-Ion Battery Detector |  | Unavailable | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | EWIS Panels |  | EWIS panel | Input |  |  |  |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Speakers | Standard Speaker, Horn Speaker | Speaker | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Warden Intercom Point |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | Visual Warning System | Visual Alarm Devices |  | Visual alarm device | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
2 | Means of Warning | Audible Warning System | Sounders |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | units
2 | Means of Warning | Fire Alarm Cabling | EWIS Fire-Rated Cabling |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
3 | Means of Egress | Emergency Lighting System | Emergency Luminaires |  | Emergency Luminaire | Input |  |  | Total Quantity,Grid Spacing,Coverage Area |  | units
3 | Means of Egress | Exit Signage System | Exit Signs | Illuminated Exit Sign, Directional Exit Sign | Illuminated Exit Sign | Input |  |  | Total Quantity |  | units
4 | Means of First Aid Fire-Fighting | Portable Extinguisher System | Extinguishers | CO₂, Dry Powder, Water, Wet Chemical | Fire extinguishers | Input |  |  |  |  | units
4 | Means of First Aid Fire-Fighting | Fire Blanket | Fire Blanket | 0.9m X 0.9m, 1.8m X 1.8m |  | Unavailable
4 | Means of First Aid Fire-Fighting | Hose Reels | Hose Reel Assembly | 19 mm hose reel, 25 mm hose reel | Hose reel , Cabinet, Fire Hose Reel, Hose reel valve | Input |  |  |  |  | reels
4 | Means of First Aid Fire-Fighting | Hose Reels | Hose Reel Pipework | Copper, Galvanised mild steel, HDPE | Pipework | Input |  |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Plasterboard Wall Assembly |  | Fire Resistant Plasterboard | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Speed Panel Wall Assembly |  | Speed Panel | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Masonry Wall Assembly |  | Masonry | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Concrete Wall Assembly |  | Concrete | Input | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  |  |  | m2 | [6 empty] | Y
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors |  | Fire Door | Input |  |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors (Steel with Glazing) |  | Fire Door(Steel with Glazing) | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Resistant Glazing |  | Glass Glazing | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Smoke Doors |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | doors
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Shutters |  | Fire Shutter | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Curtains |  | Fire Curtain | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Duct Penetration Protection | Fusible-Link Fire Damper |  | Fusible link damper | Input | Ensure the selected product's size is suitable for the actual duct size being protected. |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire Batts |  | Mastic Fire batt | Input |  |  |  |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Collars |  | Fire collar | Input | Ensure the selected product's size is suitable for the actual pipe diameter being protected. |  |  |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Joint Seals |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Pipe Wraps |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Mastic |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Intumescent Coating |  | Intumescent coating | Input |  |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Spray-Applied Fire Protection |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available. |  |  |  | m2
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Heads | Exposed, Concealed, Semi-Recessed, Sidewall | Sprinkler Head | Input |  |  | Total Quantity,Grid Spacing,Coverage Area | Y | units
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Pipework |  | Sprinkler Pipework | Input | The Formula option is an early-stage geometric approximation, not a cited AS clause - verify before relying on it for design. |  | Total Quantity,Formula |  | m
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Valves |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Sprinkler Heads |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Dry Pipework |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Valve Assembly |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Nitrogen Generator |  |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Fire Water Supply Equipment | Water Tank | Reinforced Concrete, Stainless Steel |  | Unavailable | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Fire Water Supply Equipment | Main Fire Pump Set | Electric-Driven, Diesel-Driven | Pump sets | Input |  |  |  |  | kg
6 | Means of Suppression | Fire Water Supply Equipment | Jockey Pump Set |  |  | Input | Future Implmentation: Embodied carbon data is not currently available. This apparatus is excluded from the current estimate.
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Exhaust Fan |  | Smoke Exhaust Fan (notional - 1000mm) | Input |  |  |  |  | kg
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Subducts |  | Smoke Subducts | Input | Ensure the selected product matches the desired duct size. |  |  |  | m2
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Motorised Smoke Dampers |  | Motorized Dampers | Input | Ensure the selected product's size is suitable for the actual duct size being protected. |  |  |  | units
8 | Means of Fire Brigade Access and Intervention | Hydrants | Hydrants |  | Hydrants | Input
8 | Means of Fire Brigade Access and Intervention | Hydrants | Hydrant Pipework |  | Hydrant Pipework | Input |  |  |  |  | m
8 | Means of Fire Brigade Access and Intervention | Hydrants | Hydrant Boosters |  |  | Unavailable | Typically 1 booster assembly per hydrant system - confirm against site layout and AS2419.1. |  |  |  | boosters
9 | Fire Safety Management | Fire Safety Signage and Information | Regulatory and Operational Signs | No-Storage Sign, Keep-Clear Sign, Fire-Door Sign | Fire safety signage system | Input |  |  |  |  | units
9 | Fire Safety Management | Fire Safety Signage and Information | Evacuation Diagrams | Standard Evacuation Diagram | Evacuation Diagram System | Unavailable |  |  |  |  | systems
9 | Fire Safety Management | Fire Safety Signage and Information | Fire Equipment Identification Signs | Extinguisher, Hose Reel, Hydrant | Fire Equipment Identification Sign | Unavailable | [10 empty] | Extinguishers,Hose Reel Assembly,Hydrants,Hydrant Boosters
10 | Special Hazards | Special Hazard Systems | Data-Centre Gaseous Suppression Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Battery Energy Storage Fire Protection Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Commercial Kitchen Suppression Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Carpark Special Detection Systems |  |  | Unavailable
10 | Special Hazards | Special Hazard Systems | Atrium Fire and Smoke-Control Systems |  |  | Unavailable