## Input
User input
Input | Value | Unit | Sprinklers | Yes | Yes / No | *Sprinkler pipework allowance is not directly prescribed by AS 2118.1. The tool uses an AS-informed sprinkler spacing basis and applies a project-adjustable routing factor for early-stage pipework estimation.
NCC building class | 5 |  | Sprinkler protected area, m² | 1000 | default = total protected floor area
Floor area per storey, m² | 1000 | m^2 | Sprinkler hazard classification | High Hazard | Light Hazard / Ordinary Hazard / High Hazard / user-defined | Sprinkler pipe length, m
Number of storeys | 4 | storeys | Sprinkler coverage basis | Full | Full / user-defined | = N_risers × N_storeys × floor-to-floor height + k_sprinkler × protected floor area / √(sprinkler spacing area)
Effective height, m | 20 | m | Sprinkler head spacing or area per head, m² | 9 | default from AS assumption, override allowed
Floor-to-floor height, m | 2 |  | Pipework allowance | 37008 | default factor, override allowed
Number of exits per storey | 3 |  | Sprinkler head count | 111
Sprinkler hazard classification | High Hazard |  | Actual sprinkler head count override |  | optional
|  |  | Hose reels | Yes | Yes / No
System | Input |  | Hose reel served area, m² | 1000 | default = total protected floor area
Sprinklers | No / Full |  | Hose reel coverage basis | ? | default AS-based coverage / user-defined | Sprinkler head
Hydrants | Yes / No |  | Pipework allowance |  | default factor / override | Sprinkler protected area, m² | Sprinkler head spacing or area per head, m² | Sprinkler head count
Hose reels | Yes / No |  | Hose reel count |  |  | 100 | 12 | 83
Extinguishers | Yes / No |  | Hose reel count override |  | optional | Sprinkler pipe length, m
Detection system | None / Type |  |  |  | ` |  |  | pipe length
Alarm/warning system | None / Type |  | Extinguishers | Yes | Yes / No |  |  | 1000m
Emergency lighting | Yes / No |  | Fire class basis | A | A / B / C / E / F
Exit signs | Yes / No |  | Hazard level | High Hazard | Ordinary / high / special risk
|  |  | Extinguisher type |  | ABE powder / CO₂ / foam / wet chemical / water
|  |  | Special risk areas included |  | switch room, kitchen, plant, server room
Extinguisher count
|  |  | Extinguisher count override |  | optional
Initial user input |  |  | Emergency lighting | Yes / No
Secondary user input |  |  | Emergency lighting area, m² | 1000 | default = total protected floor area
From Australian Standards |  |  | Number of exits | 3 | from general input
Output |  |  | Number of stairs | #REF! | from general input
Optional override |  |  | Egress corridor allowance |  | default factor / override
|  |  | Luminaire count override |  | optional
|  |  | Hydrants | Yes / No
|  |  | Hydrant served levels | 4 | all levels / selected levels
|  |  | Number of risers |  | default from stairs/storeys, override allowed
|  |  | Hydrant outlet count |  | default estimate, override allowed
|  |  | Booster included |  | Yes / No / unknown
|  |  | Pump/tank included |  | Yes / No / unknown
|  |  | Pipe length override |  | optional
|  |  | Exit signs | Yes / No
|  |  | Number of exits | 3 | from general input
|  |  | Number of direction changes |  | default factor / override
|  |  | Number of storeys | 4 | from general input
|  |  | Exit sign count | 12
|  |  | Exit sign count override |  | optional
|  |  | Alarm/warning system type |  | None / Sounders / Speakers / EWIS / Other
|  |  | Warning system type |  | sounders / speakers / EWIS
|  |  | Warning protected area, m² | 1000 | default = total protected floor area
|  |  | Device coverage basis |  | default allowance / override
|  |  | Visual alarm devices included |  | Yes / No
|  |  | Alarm device count override |  | optional
|  |  | Detection system type |  | None / Smoke / Heat / Smoke + heat / Other
|  |  | Detection protected area, m² | 1000 | default = total protected floor area
|  |  | Detector type | Smoke | Smoke / Heat / Aspirating
|  |  | Detector spacing or coverage area | 104.04 | default AS-based / override
|  |  | Number of zones |  | default by storey / override
|  |  | Manual call points included |  | Yes / No
|  |  | Detector count override |  | optional
Note on B14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Implemented in code

## Database
system | component | parameter | option | default_value | unit | evidence_level | source_basis | override
sprinkler | sprinkler_head | spacing_area | Light Hazard | 21 | m²/head | B | AS 2118.1 hazard-based spacing, team-confirmed | Yes
sprinkler | sprinkler_head | spacing_area | Ordinary Hazard | 12 | m²/head | B | AS 2118.1 hazard-based spacing, team-confirmed | Yes
sprinkler | sprinkler_head | spacing_area | High Hazard | 9 | m²/head | B | AS 2118.1 hazard-based spacing, team-confirmed | Yes
sprinkler | sprinkler_head | count_rounding | default | ROUNDUP | method | C | Derived quantity formula | No
sprinkler | sprinkler_head | quantity_formula | default | ROUNDUP(sprinkler_protected_area / spacing_area, 0) | formula | C | AS2118.1 hazard-based spacing area converted to sprinkler head count | Yes
sprinkler | pump | pump_count | <25m | 0 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
sprinkler | pump | pump_count | >25m | 1 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
sprinkler | pipework | default_risers | default | 1 | no. | D | Early-stage assumption | Yes
sprinkler | pipework | pipe_routing_factor | low | 1.1 | multiplier | D | Layout assumption | Yes
sprinkler | pipework | pipe_routing_factor | medium | 1.3 | multiplier | D | Layout assumption | Yes
sprinkler | pipework | pipe_routing_factor | high | 1.6 | multiplier | D | Layout assumption | Yes
sprinkler | pipework | drop_length_per_head | default | 0 | m/head | D | Baseline excludes drops to avoid double-counting | Yes
sprinkler | pipework | vertical_riser_formula | default | risers × storeys × floor_to_floor_height | formula | C/D | Derived from building geometry | Yes
sprinkler | pipework | horizontal_pipe_formula | default | routing_factor × area / SQRT(spacing_area) | formula | C/D | Grid-based approximation from sprinkler spacing | Yes
hydrant | hydrant_riser | default_risers | default | MAX(1, number_of_fire_stairs) | formula | D | Simplified proxy based on internal hydrants commonly being located within or adjacent to fire-isolated exits/fire stairs under AS2419.1 location logic; not a direct AS quantity rule | Yes
hydrant | hydrant_outlet | quantity_formula | default | MAX(1, number_of_fire_stairs) × number_of_storeys × outlets_per_riser_per_storey | formula | C/D | Simplified riser-per-storey method using fire stairs as the default riser proxy; actual hydrant layout requires AS2419.1 coverage assessment | Yes
hydrant | hydrant_outlet | outlets_per_riser_per_storey | default | 1 | no/riser/storey | D | Simplified early-stage assumption for internal hydrant outlets; actual outlet count depends on AS2419.1 coverage and layout | Yes
hydrant | booster | booster_count | default | IF(hydrants_selected,1,0) | no | D | Typical hydrant system allowance; final booster arrangement is project-specific | Yes
hydrant | pump | pump_count | <50m | 0 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
hydrant | pump | pump_count | >50m | 1 | no | D | Not included in baseline; pump requirement depends on hydraulic design and available water supply | Yes
hydrant | pipework | vertical_riser_formula | default | hydrant_risers × served_storeys × floor_to_floor_height | formula | C/D | Geometry-derived vertical hydrant riser allowance | Yes
hydrant | pipework | horizontal_run_factor | default | 0.5 | multiplier | D | Average horizontal run approximated as 0.5 × SQRT(floor_plate_area) where actual routing is unknown | Yes
hydrant | pipework | horizontal_pipe_formula | default | hydrant_risers × horizontal_run_factor × SQRT(floor_plate_area) | formula | D | Layout approximation for early-stage pipework estimate from booster/feed to riser zone | Yes
hydrant | pipework | total_pipe_formula | default | (hydrant_risers × served_storeys × floor_to_floor_height) + (hydrant_risers × horizontal_run_factor × SQRT(floor_plate_area)) | formula | C/D | Vertical riser allowance plus simplified horizontal feed allowance | Yes
hose_reel | hose_reel | hose_length | default | 36 | m | B/C | AS2441 system coverage basis - 36 m hose length, verify against AS2441 | Yes
hose_reel | hose_reel | spray_allowance | default | 4 | m | B/C | AS2441 system coverage basis - 4 m spray allowance, verify against AS2441 | Yes
hose_reel | hose_reel | effective_reach | default | 40 | m path reach | B/C | AS2441 system coverage basis: 36 m hose + 4 m spray | Yes
hose_reel | hose_reel | location_basis | default | within 4 m of exit | text | B/C | AS2441 location basis, verify against AS2441 | No
hose_reel | hose_reel | min_reels_per_storey | default | 1 | no/storey | D | Simplified early-stage allowance where hose reels are selected | Yes
hose_reel | hose_reel | effective_area_per_reel | default | 400 | m^2/reel | D | Estimate from: https://cccengineering.com.au/design-memos/fire-hydrant-hose-reel-requirements/ | Yes
hose_reel | hose_reel | quantity_formula | default | number_of_storeys × MAX(1, ROUNDUP(floor_area_per_storey / effective_area_per_reel, 0)) | formula | C/D | AS2441 40 m system coverage simplified to early-stage area allowance | Yes
hose_reel | pipework | default_risers | default | 1 | no | D | Early-stage assumption unless riser count is known | Yes
hose_reel | pipework | vertical_pipe_formula | default | default_risers × number_of_storeys × floor_to_floor_height | formula | C/D | Geometry-derived riser allowance | Yes
hose_reel | pipework | horizontal_run_factor | default | 0.5 | multiplier | D | Average horizontal run approximated as 0.5 × SQRT(floor_plate_area) | Yes
hose_reel | pipework | horizontal_pipe_formula | default | hose_reel_count × horizontal_run_factor × SQRT(floor_plate_area) | formula | D | Layout approximation for early-stage pipework estimate | Yes
hose_reel | pipework | total_pipe_formula | default | (default_risers × number_of_storeys × floor_to_floor_height) + (hose_reel_count × horizontal_run_factor × SQRT(floor_plate_area)) | formula | C/D | Vertical riser allowance plus simplified horizontal distribution allowance | Yes
hose_reel | pipework | nominal_pipe_diameter | default | DN25 | pipe size | B/C | AS2441-informed secondary source - hose reel supply pipe minimum DN25, verify against AS2441 | Yes
hose_reel | cabinet | cabinet_quantity_formula | default | hose_reel_count | formula | D | Optional cabinet allowance; include only where hose reel cabinets are assumed in carbon database | Yes
extinguisher | portable_extinguisher | representative_product | Default | 6 kg powder extinguisher - 34A 233BC | type | C | EPD-IES-0019486 product family | Yes
extinguisher | portable_extinguisher | representative_rating | Default | 34A 233BC | rating | C | EPD-IES-0019486 product identification | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class A ¦ No fixed suppression ¦ 34A representative product | 675 | m2/extinguisher | B | AS2444 Table 4.1 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class A ¦ Fixed suppression ¦ 34A representative product | 1000 | m2/extinguisher | B | AS2444 Table 4.1 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | class_A_quantity_formula | default | number_of_storeys × ROUNDUP(floor_area / class_A_max_floor_area_per_extinguisher, 0) | formula | C | AS2444 Table 4.1 area basis applied floor-by-floor | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Light ¦ No fixed suppression ¦ 233B representative product | 80 | m2/extinguisher | B | AS2444 Table 4.2 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Light ¦ Fixed suppression ¦ 233B representative product | 150 | m2/extinguisher | B | AS2444 Table 4.3 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Ordinary ¦ No fixed suppression ¦ 233B representative product | 150 | m2/extinguisher | B | AS2444 Table 4.2 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ Ordinary ¦ Fixed suppression ¦ 233B representative product | 300 | m2/extinguisher | B | AS2444 Table 4.3 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ High ¦ No fixed suppression ¦ 233B representative product | 300 | m2/extinguisher | B | AS2444 Table 4.2 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | max_floor_area_per_extinguisher | Class B ¦ High ¦ Fixed suppression ¦ 233B representative product | 300 | m2/extinguisher | B | AS2444 Table 4.3 - higher rating permitted under Clause 4.1 | Yes
extinguisher | portable_extinguisher | class_B_quantity_formula | default | ROUNDUP(class_B_risk_area / class_B_max_floor_area_per_extinguisher, 0) | formula | C | AS2444 Table 4.2 and Table 4.3 area basis | Yes
extinguisher | portable_extinguisher | total_quantity_formula | default | class_A_extinguisher_quantity + class_B_extinguisher_quantity | formula | C | Simplified estimator aggregation | Yes
detection | smoke_detector | coverage_area | Smoke detectors | 104.04 | m2/detector | B | AS1670.1 detector spacing basis; 10.2 m × 10.2 m coverage area used for simplified estimator | Yes
detection | heat_detector | coverage_area | Heat detectors | 51.84 | m2/detector | B | AS1670.1 detector spacing basis; 7.2 m × 7.2 m coverage area used for simplified estimator | Yes
detection | aspirating_detection | coverage_area | Aspirating detection | 2000 | m2/system | D | Simplified early-stage allowance; aspirating detection layout depends on pipe network design and sampling points | Yes
detection | detection_device | quantity_formula | Smoke detectors | ROUNDUP(detection_protected_area / 104.04, 0) | formula | C | AS1670.1 spacing basis converted to area-based quantity estimate | Yes
detection | detection_device | quantity_formula | Heat detectors | ROUNDUP(detection_protected_area / 51.84, 0) | formula | C | AS1670.1 spacing basis converted to area-based quantity estimate | Yes
detection | detection_device | quantity_formula | Aspirating detection | ROUNDUP(detection_protected_area / 2000, 0) | formula | D | Simplified early-stage allowance; actual aspirating detection design requires specialist layout | Yes
detection | fire_indicator_panel | count_formula | default | IF(detection_selected, 1, 0) | no | C/D | Typical system-level allowance; most detection systems require a central indicating/control panel | Yes
detection | manual_call_point | count_formula | default | number_of_storeys × MAX(1, number_of_exits_per_storey) | no | C/D | Simplified allowance based on one manual call point per exit route per storey; actual placement requires AS1670.1 layout assessment | Yes
alarm_warning | sounder | coverage_area | Sounders | 250 | m2/device | D | Simplified audibility proxy; AS1670.4 is performance/design based and does not provide a simple m2/device estimator | Yes
alarm_warning | speaker | coverage_area | Speakers / EWIS | 200 | m2/device | D | Simplified speech/warning coverage proxy; actual speaker quantity depends on acoustic design and intelligibility requirements | Yes
alarm_warning | strobe | coverage_area | Visual alarm devices | 250 | m2/device | D | Simplified visual alarm proxy; actual requirement depends on occupancy, accessibility and layout | Yes
alarm_warning | warning_device | quantity_formula | Sounders | ROUNDUP(warning_protected_area / 250, 0) | formula | D | Area-based proxy for early-stage estimator; actual compliance requires AS1670.4 acoustic performance assessment | Yes
alarm_warning | warning_device | quantity_formula | Speakers / EWIS | ROUNDUP(warning_protected_area / 200, 0) | formula | D | Area-based proxy for early-stage estimator; actual compliance requires AS1670.4 acoustic and intelligibility assessment | Yes
alarm_warning | visual_alarm_device | quantity_formula | Visual alarm devices | ROUNDUP(warning_protected_area / 250, 0) | formula | D | Optional area-based proxy where visual alarms are selected | Yes
alarm_warning | control_panel | count_formula | default | IF(alarm_warning_selected, 1, 0) | no | C/D | Typical system-level allowance for alarm/warning control equipment | Yes
emergency_lighting | emergency_luminaire | effective_area_per_luminaire | default | 100 | m2/luminaire | D | Simplified emergency lighting density proxy; AS/NZS2293.1 is photometric/layout based rather than m2/luminaire based | Yes
emergency_lighting | emergency_luminaire | quantity_formula | default | number_of_storeys × MAX(1, ROUNDUP((total_protected_floor_area / number_of_storeys) / effective_area_per_luminaire, 0)) | formula | D | Area-based proxy for early-stage estimator; actual compliance requires AS/NZS2293.1 emergency lighting layout and photometric assessment | Yes
emergency_lighting | stair_luminaire | luminaires_per_stair_per_storey | default | 1 | no/stair/storey | D | Simplified allowance for emergency lighting to stairs; actual layout depends on stair geometry and luminaire spacing | Yes
emergency_lighting | stair_luminaire | quantity_formula | default | number_of_stairs × number_of_storeys × luminaires_per_stair_per_storey | formula | D | Simplified stair lighting allowance for early-stage carbon estimation | Yes
emergency_lighting | total_luminaire | total_quantity_formula | default | emergency_luminaire_count + stair_luminaire_count | formula | D | Aggregated early-stage emergency luminaire estimate | Yes
exit_signs | exit_sign | signs_per_exit | default | 1 | no/exit | C/D | Simplified allowance based on illuminated exit signage at required exits; actual sign placement requires AS/NZS2293.1 layout assessment | Yes
exit_signs | exit_sign | exit_sign_quantity_formula | default | number_of_storeys × number_of_exits_per_storey × signs_per_exit | formula | C/D | Required-exit based estimate; actual compliance requires exit path and sign visibility assessment under AS/NZS2293.1 | Yes
exit_signs | directional_sign | directional_sign_area_allowance | default | 500 | m2/directional sign | D | Simplified wayfinding proxy where exit path direction changes are unknown | Yes
exit_signs | directional_sign | directional_sign_quantity_formula | default | number_of_storeys × ROUNDUP((total_protected_floor_area / number_of_storeys) / directional_sign_area_allowance, 0) | formula | D | Area-based proxy for directional signs where detailed egress path layout is unavailable | Yes
exit_signs | total_exit_sign | total_quantity_formula | default | exit_sign_count + directional_sign_count | formula | D | Aggregated early-stage exit signage estimate | Yes
Exhaust systems | Smoke_exhaust_fan | Fans_per_floor | Adjoined by class 2, 3, 9 building | number_of_storeys x 3 | formula | C | AS 1668.1, section 9.4.2
Exhaust systems | Smoke_exhaust_fan | Fans_per_floor | Not adjoined by class 2, 3 or 9 | number_of_storeys x 2 | formula | C | AS 1668.1, section 9.4.2

## csv
lookup_id | system | component | parameter | condition_type | condition_hazard | condition_threshold_state | condition_selection | value | unit | evidence_level | override_allowed | active | source_basis | notes
sprinkler.required_flag.triggered | sprinkler | sprinkler_system | required_flag | system_required |  | triggered |  | 1 | boolean | A | No | Yes | NCC sprinkler trigger basis; use decision_rules.csv to test threshold, not to calculate sprinkler head quantity. | Used by Python after decision rule evaluates true.
sprinkler.required_flag.not_triggered | sprinkler | sprinkler_system | required_flag | system_required |  | not_triggered |  | 0 | boolean | A | No | Yes | NCC sprinkler trigger basis; use decision_rules.csv to test threshold, not to calculate sprinkler head quantity. | Used by Python after decision rule evaluates false.
sprinkler.spacing_area.light_hazard | sprinkler | sprinkler_head | spacing_area | hazard_class | Light Hazard |  |  | 21 | m2/head | B | Yes | Yes | AS 2118.1 hazard-based sprinkler spacing; team-confirmed simplified value. | Python: ceil(sprinkler_protected_area / spacing_area).
sprinkler.spacing_area.ordinary_hazard | sprinkler | sprinkler_head | spacing_area | hazard_class | Ordinary Hazard |  |  | 12 | m2/head | B | Yes | Yes | AS 2118.1 hazard-based sprinkler spacing; team-confirmed simplified value. | Python: ceil(sprinkler_protected_area / spacing_area).
sprinkler.spacing_area.high_hazard | sprinkler | sprinkler_head | spacing_area | hazard_class | High Hazard |  |  | 9 | m2/head | B | Yes | Yes | AS 2118.1 hazard-based sprinkler spacing; team-confirmed simplified value. | Python: ceil(sprinkler_protected_area / spacing_area).
sprinkler.pump_count.above_threshold | sprinkler | pump | pump_count | pump_threshold |  | above_threshold |  | 1 | no | D | Yes | No | Inactive simplified pump allowance only; pump requirement depends on hydraulic design and available water supply. | Kept as future implementation value; not used in current baseline.
sprinkler.pump_count.at_or_below_threshold | sprinkler | pump | pump_count | pump_threshold |  | at_or_below_threshold |  | 0 | no | D | Yes | No | Inactive simplified pump allowance only; pump requirement depends on hydraulic design and available water supply. | Kept as future implementation value; not used in current baseline.
hydrant.required_flag.triggered | hydrant | hydrant_system | required_flag | system_required |  | triggered |  | 1 | boolean | A/C | No | Yes | NCC hydrant trigger basis; use decision_rules.csv to test threshold, not to calculate outlet quantity. | Assumes normal fire brigade access context; verify NCC class/exemptions for final design.
hydrant.required_flag.not_triggered | hydrant | hydrant_system | required_flag | system_required |  | not_triggered |  | 0 | boolean | A/C | No | Yes | NCC hydrant trigger basis; use decision_rules.csv to test threshold, not to calculate outlet quantity. | Assumes normal fire brigade access context; verify NCC class/exemptions for final design.
hydrant.riser.min_risers | hydrant | hydrant_riser | min_risers | default |  |  |  | 1 | no | D | Yes | Yes | Minimum riser allowance used with fire-stair proxy in Python calculation. | Python: hydrant_risers = max(min_risers, number_of_fire_stairs).
hydrant.outlet.outlets_per_riser_per_storey | hydrant | hydrant_outlet | outlets_per_riser_per_storey | default |  |  |  | 1 | no/riser/storey | D | Yes | Yes | Simplified early-stage assumption for internal hydrant outlets; actual outlet count depends on AS 2419.1 coverage and layout. | Python: outlet_count = risers * storeys * outlets_per_riser_per_storey.
hydrant.booster.count_if_selected | hydrant | booster | booster_count | system_selection |  |  | selected | 1 | no | D | Yes | Yes | Typical hydrant system allowance; final booster arrangement is project-specific. | Python returns 1 booster if hydrant system is included.
hydrant.pump_count.above_threshold | hydrant | pump | pump_count | pump_threshold |  | above_threshold |  | 1 | no | D | Yes | No | Inactive simplified pump allowance only; pump requirement depends on hydraulic design and available water supply. | Kept as future implementation value; not used in current baseline.
hydrant.pump_count.at_or_below_threshold | hydrant | pump | pump_count | pump_threshold |  | at_or_below_threshold |  | 0 | no | D | Yes | No | Inactive simplified pump allowance only; pump requirement depends on hydraulic design and available water supply. | Kept as future implementation value; not used in current baseline.

## decision_rules
rule_id | system | component | output_parameter | input_variable | operator | threshold_value | threshold_unit | true_value | false_value | value_unit | evidence_level | source_basis | active | notes
sprinkler.required.effective_height_gt_25m | sprinkler | sprinkler_system | system_required | effective_height | > | 25 | m | 1 | 0 | boolean | A | NCC 2022 sprinkler trigger: effective height over 25 m; check class-specific exceptions/concessions before final design. | Yes | Use as system trigger/warning, not as sprinkler head quantity. Quantity still calculated from protected area and spacing area.
hydrant.required.total_floor_area_gt_500m2 | hydrant | hydrant_system | system_required | total_protected_floor_area | > | 500 | m2 | 1 | 0 | boolean | A/C | NCC/AS2419.1 hydrant trigger simplified as building floor area over 500 m2; verify NCC class/exemption details. | Yes | Use as system trigger/warning. Hydrant outlet quantity still uses simplified riser-per-storey method.
sprinkler.pump_count.effective_height_gt_25m | sprinkler | pump | pump_count | effective_height | > | 25 | m | 1 | 0 | no | D | Previous simplified pump allowance only. Pump requirement depends on hydraulic design and water supply; not used in current baseline. | No | Inactive because pumps are excluded from the current carbon scope.
hydrant.pump_count.effective_height_gt_50m | hydrant | pump | pump_count | effective_height | > | 50 | m | 1 | 0 | no | D | Previous simplified pump allowance only. Pump requirement depends on hydraulic design and water supply; not used in current baseline. | No | Inactive because pumps are excluded from the current carbon scope.

## Tracker
System | Apparatus | Component | Note | EC source status | Formula status | Formula | GUI status
1. Means of detection | Automatic smoke detection system | Smoke detector |  | Found – generic | Draft |  | Not started
| Aspirating smoke detectors | Aspirating unit |  | Found – generic | Draft |  | Not started
|  | Sampling pipework |  | Not started | Not started |  | Not started
|  | Sampling points (Do we need this?) |  | Not started | Not started |  | Not started
| Heat detection system | Heat detector |  | Found – generic | Draft |  | Not started
| Manual alarm initiation system | Manual call point |  | Not started | Draft | 1 per 30m | Not started
| Fire detection control system | Fire indicator panel |  | Found – product-specific | Draft | 1 per building | Not started
2. Means of warning | EWIS / voice alarm system | Speakers |  | Not started | Not started | 1 per area? | Not started
|  | EWIS panel | Might be same thing as fire indicator panel | Not started | Draft | 1 per building | Not started
|  | Amplifiers |  | Not started | Not started | 1 per area? | Not started
|  | Cabling | Fire-rated | Not started | Not started |  | Not started
|  |  | Non-fire-rated | Found – product-specific | Not started |  | Not started
| Visual warning system | Visual alarm device |  | Not started | Not started |  | Not started
| Occupant warning system | Sounders |  | Not started | Not started |  | Not started
3. Means of egress | Emergency lighting system | Emergency luminaire |  | Not started | Not started |  | Not started
| Exit signage system | Illuminated exit sign |  | Found – product-specific | Draft | 1 per exit | Not started
|  | Directional exit sign |  | Not started | Not started |  | Not started
4. Means of first-aid fire-fighting | Fire hose reel system | Hose reel assembly |  | Found – generic | Draft | 1 per exits | Not started
|  | Cabinet |  | Found – generic | Draft | 1 per hose reel | Not started
|  | Pipework |  | Not started | Not started |  | Not started
| Portable extinguisher system | Portable extinguisher |  | Found – product-specific | Draft | floor_area / protected_area | Not started
|  | Bracket |  | Not started | Draft | 1 per extinguisher | Not started
|  | Cabinet |  | Not started | Draft | 1 per extinguisher | Not started
5. Means of restricting fire spread / structural protection | Fire-rated wall system | Wall assembly | Plasterboard | Found – generic | Not started | Material * thickness * area? | Not started
|  |  | Speedpanel | Found – generic | Not started | Material * thickness * area? | Not started
|  |  | Masonry | Found – generic | Not started | Material * thickness * area? | Not started
|  |  | Concrete | Found – generic | Not started | Material * thickness * area? | Not started
| Penetration fire-stopping system | Fire batt |  | Found – product-specific | Manual Input | How? | Not started
| Pipe penetration protection system | Intumescent collar |  | Found – product-specific | Manual Input | How? | Not started
|  | Intumescent pipe wrap |  | Not started | Manual Input | How? | Not started
| Fire/smoke damper system | Fusible-link fire damper |  | Found – generic | Manual Input | How? | Not started
|  | Motorised fire/smoke damper |  | Found – product-specific | Manual Input | How? | Not started
| Spray-applied fire protection system | Vermiculite spray |  | Not started | Manual Input | How? | Not started
| Intumescent coating system | Intumescent coating |  | Found – product-specific | Manual Input | How? | Not started
| Door system | Fire-door |  | Found – product-specific | Draft | 1 per door | Not started
|  | Smoke-door |  | Not started | Draft | 1 per door | Not started
| Fire-resistant glazing system | Fire-resistant glazing assembly |  | Found – generic | Manual Input | # * material * area(m2) | Not started
| Fire shutter system | Fire shutter assembly |  | Found – product-specific | Manual Input | # * material * area(m2) | Not started
| Fire curtain system | Fire curtain |  | Found – product-specific | Manual Input | # * material * area(m2) | Not started
6. Means of suppression | Automatic sprinkler system | Sprinkler head | Raindrop | Found – product-specific | Draft |  | Not started
|  |  | Wall-wetting | Not started | Draft |  | Not started
|  | Sprinkler pipework |  | Found – product-specific | Not started |  | Not started
|  | Valve assembly |  | Not started | Not started |  | Not started
|  | Booster assembly |  | Not started | Not started |  | Not started
|  | Pump |  | Not started | Not started |  | Not started
| Hydrant system | Hydrant outlet |  | Found – generic | Not started |  | Not started
|  | Hydrant pipework |  | Not started | Not started |  | Not started
|  | Booster assembly |  | Not started | Not started |  | Not started
|  | Pump |  | Not started | Not started |  | Not started
7. Means of smoke hazard management | Smoke exhaust and pressurisation system | Smoke exhaust fan |  | Found – generic | Manual Input | Total # | Not started
|  | Fire-resistant ductwork |  | Not started | Manual Input | material * area(m2) | Not started
|  | Regular sheet-metal ductwork |  | Found – generic | Manual Input | material * area(m2) | Not started
8. Means of fire brigade access and intervention | Fire control centre | Future extension
| Fire service lift controls | Future extension
9. Fire safety management | Fire safety signage system | No-storage sign | Aluminium | Found – generic | Manual Input | # * material * area(m2) | Not started
|  | Keep-clear sign | Aluminium | Found – generic | Manual Input | # * material * area(m2) | Not started
|  | Fire-door sign | Aluminium | Found – generic | Manual Input | # * material * area(m2) | Not started
| Evacuation diagram system | Evacuation diagram | Aluminium | Found – generic | Manual Input | # * material * area(m2) | Not started
| Fire equipment identification signage system | Fire extinguisher sign | Aluminium | Found – generic | Manual Input | # * material * area(m2) | Not started
|  | Hose reel sign | Aluminium | Found – generic | Manual Input | # * material * area(m2) | Not started
|  | Hydrant sign | Aluminium | Found – generic | Manual Input | # * material * area(m2) | Not started
10. Special hazards | Data-centre gaseous suppression system | Future extension
| Battery-energy-storage fire protection system | Future extension
| Commercial kitchen suppression system | Future extension
| Carpark special detection system | Future extension
| Atrium fire and smoke-control system | Future extension
Note on E25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need more variation for various FRLs