## calc_rules
system | component | parameter | condition_key | condition_value | value | unit | notes
sprinkler | sprinkler_head | spacing_area | hazard_class | Light Hazard | 21 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | spacing_area | hazard_class | Ordinary Hazard | 12 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | spacing_area | hazard_class | High Hazard | 9 | m2/head | AS 2118.1 hazard-based spacing
sprinkler | sprinkler_head | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / spacing_area, 0) | formula | Area / spacing, rounded up
sprinkler | pipework | default_risers | default | default | 1 | no. | Fallback only - real Risers input from Project Info takes priority
sprinkler | pipework | vertical_riser_formula | default | default | FORMULA: risers * storeys * floor_to_floor_height | formula | UNVERIFIED assumption - derived from building geometry, not a cited AS clause. Confirm before relying on it.
sprinkler | pipework | horizontal_pipe_formula | default | default | FORMULA: protected_area / SQRT(spacing_area) | formula | UNVERIFIED assumption - grid-based approximation from sprinkler spacing, not a cited AS clause. Confirm before relying on it.
hose_reel | hose_reel | effective_area_per_reel | default | default | 400 | m2/reel | Coverage-based allowance (see source reference in notes)
hose_reel | hose_reel | quantity_formula | default | default | FORMULA: storeys * MAX(1, ROUNDUP(area_per_storey / effective_area_per_reel, 0)) | formula | Per-storey coverage allowance
hose_reel | cabinet | cabinet_quantity_formula | default | default | FORMULA: hose_reel_count | formula | Definitional: cabinets always equal hose reel count
detection | smoke_detector | coverage_area | default | default | 104.04 | m2/detector | AS1670.1 10.2m x 10.2m coverage
detection | heat_detector | coverage_area | default | default | 51.84 | m2/detector | AS1670.1 7.2m x 7.2m coverage
detection | aspirating_detection | coverage_area | default | default | 2000 | m2/system | Simplified early-stage allowance - not a specific AS clause
detection | detection_device | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area / coverage, rounded up
detection | fire_indicator_panel | count_formula | default | default | FORMULA: IF(detection_selected, 1, 0) | formula | One panel per detection system
detection | manual_call_point | count_formula | default | default | FORMULA: storeys * MAX(1, exits_per_storey) | formula | One per exit route per storey
extinguisher | portable_extinguisher | quantity_formula | default | default | FORMULA: storeys * ROUNDUP((floor_area / storeys) / max_area, 0) | formula | AS2444 area basis applied floor-by-floor, using the max area for the selected (hazard, rating, suppression) combination
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | Light | 1A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | Ordinary | 2A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_a | hazard_class | High | 2A | rating | AS2444 Table 4.1 - minimum acceptable rating
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦1A | 100 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦2A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦3A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Light¦4A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦2A | 100 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦3A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦4A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | Ordinary¦6A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦2A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦3A | 200 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦4A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦6A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_no_suppression | hazard_rating | High¦10A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦1A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦2A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦3A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Light¦4A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦2A | 150 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦3A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦4A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | Ordinary¦6A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦2A | 225 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦3A | 300 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦4A | 450 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦6A | 675 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | max_area_class_a_with_suppression | hazard_rating | High¦10A | 1000 | m2 | AS2444 Table 4.1
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | Light | 5B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | Ordinary | 20B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | min_rating_class_b | hazard_class | High | 40B | rating | AS2444 Table 4.2 - minimum acceptable rating
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦5B | 15 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦10B | 45 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Light¦20B | 80 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦20B | 80 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦30B | 115 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | Ordinary¦40B | 150 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦40B | 150 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦60B | 225 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_no_suppression | hazard_rating | High¦80B | 300 | m2 | AS2444 Table 4.2
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦5B | 80 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦10B | 115 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Light¦20B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦20B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦30B | 225 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | Ordinary¦40B | 300 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦40B | 150 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦60B | 225 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | max_area_class_b_with_suppression | hazard_rating | High¦80B | 300 | m2 | AS2444 Table 4.3
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦5B | 2 to 3 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦10B | 2 to 4 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Light¦20B | 2 to 5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦20B | 3 to 5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦30B | 3 to 7.5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | Ordinary¦40B | 3 to 10 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦40B | 4 to 10 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦60B | 4 to 12.5 | m | AS2444 Table 4.2
extinguisher | portable_extinguisher | travel_distance_class_b_no_suppression | hazard_rating | High¦80B | 4 to 15 | m | AS2444 Table 4.2
hydrant | hydrant_riser | min_risers | default | default | 1 | no. | Minimum riser allowance
hydrant | hydrant_outlet | outlets_per_riser_per_storey | default | default | 1 | no/riser/storey | PROXY - simplified AS2419.1 proxy, not a direct AS quantity rule
hydrant | hydrant_outlet | quantity_formula | default | default | FORMULA: risers * storeys * outlets_per_riser_per_storey | formula | Riser-per-storey method - PROXY, verify against AS2419.1 layout
hydrant | booster | booster_count | default | default | 1 | no. | Typical hydrant allowance if selected
emergency_lighting | emergency_luminaire | effective_area_per_luminaire | default | default | 100 | m2/luminaire | Density proxy - AS/NZS2293.1 is photometric-based, not m2/luminaire based
emergency_lighting | emergency_luminaire | quantity_formula | default | default | FORMULA: storeys * MAX(1, ROUNDUP((protected_area / storeys) / effective_area_per_luminaire, 0)) | formula | Area-based proxy
emergency_lighting | stair_luminaire | luminaires_per_stair_per_storey | default | default | 1 | no/stair/storey | Simplified stair allowance
emergency_lighting | stair_luminaire | quantity_formula | default | default | FORMULA: stairs * storeys * luminaires_per_stair_per_storey | formula | Stair lighting allowance
emergency_lighting | emergency_luminaire | egress_corridor_factor | default | default | 10 | multiplier | Default egress corridor allowance - user override recommended
exit_signs | exit_sign | signs_per_exit | default | default | 1 | no/exit | Simplified allowance
exit_signs | exit_sign | quantity_formula | default | default | FORMULA: storeys * exits_per_storey * signs_per_exit | formula | Required-exit based estimate
exit_signs | directional_sign | area_allowance | default | default | 500 | m2/sign | PROXY - wayfinding proxy where path layout is unavailable
exit_signs | directional_sign | quantity_formula | default | default | FORMULA: storeys * ROUNDUP((protected_area / storeys) / area_allowance, 0) | formula | Area-based proxy - low confidence
alarm_warning | sounder | coverage_area | default | default | 250 | m2/device | PROXY - AS1670.4 is performance-based, no simple m2/device estimator exists
alarm_warning | speaker | coverage_area | default | default | 200 | m2/device | PROXY - actual quantity depends on acoustic design
alarm_warning | strobe | coverage_area | default | default | 250 | m2/device | PROXY - actual requirement depends on occupancy/accessibility
alarm_warning | warning_device | quantity_formula | default | default | FORMULA: ROUNDUP(protected_area / coverage_area, 0) | formula | Area-based proxy - low confidence, verify against AS1670.4
alarm_warning | control_panel | count_formula | default | default | FORMULA: IF(alarm_warning_selected, 1, 0) | formula | One panel per system

## ui_structure
Category | Category Name | Group | Label | Apparatus | Archetype | Modes | Allow Multiple Rows | Units | Parent | Linked Mode | Formula System | Formula Component | Formula Parameters | Counted Apparatus | Disclaimer
1 | Means of Detection |  | Smoke Detectors | Smoke Detector | Input | Total Quantity,Grid Spacing,Coverage Area
1 |  |  | Heat Detectors | Heat Detector | Input | Total Quantity,Grid Spacing,Coverage Area
1 |  |  | Aspirating Units | Aspirating Unit | Input | Total Quantity,Grid Spacing,Coverage Area
1 |  | Sampling | Sampling Pipework | Sampling Pipework | Input |  |  | units
1 |  | Sampling | Sampling Points | Sampling Point | Input |  |  | units
1 |  |  | Manual Call Points | Manual Call Point | Input |  |  | units
1 |  |  | Fire Indicator Panels | Fire Indicator Panel | Input |  |  | units
2 | Means of Warning | Audio | Speakers | Speaker | Input | Total Quantity,Grid Spacing,Coverage Area
2 |  | Audio | Speaker Batteries | Battery | Linked Child |  |  |  | Speakers | Override Only
2 |  | Audio | Amplifiers | Amplifier | Input |  |  | units
2 |  | Audio | Amplifier Batteries | Battery | Linked Child |  |  |  | Amplifiers | Override Only
2 |  | Audio | Sounders | Sounder | Input | Total Quantity,Grid Spacing,Coverage Area
2 |  | Audio | Sounder Batteries | Battery | Linked Child |  |  |  | Sounders | Override Only
2 |  | Audio | Sounder Bases | Sounder Base | Linked Child |  |  |  | Sounders | Choice
2 |  | Cabling | Fire-Rated Cabling | Fire-Rated Cabling | Input |  |  | units
2 |  | Cabling | Non-Fire-Rated Cabling | Non-Fire-Rated Cabling | Input |  |  | units
2 |  | EWIS Panels | EWIS Panels | EWIS Panel | Input |  |  | units
2 |  | EWIS Panels | EWIS Panel Batteries | Battery | Linked Child |  |  |  | EWIS Panels | Override Only
2 |  | Visual Alarm Devices | Visual Alarm Devices | Visual Alarm Device | Input | Total Quantity,Grid Spacing,Coverage Area
2 |  | Visual Alarm Devices | Visual Alarm Device Batteries | Battery | Linked Child |  |  |  | Visual Alarm Devices | Override Only
2 |  | Visual Alarm Devices | Mounting Bases | Mounting Base | Linked Child |  |  |  | Visual Alarm Devices | Choice
4 | Means of First Aid Fire-Fighting | Hose Reels | Hose Reel Assembly | Hose Reel Assembly | Input |  |  | reels
4 |  | Hose Reels | Hose Reel Pipework | Pipework | Input |  |  | m
4 |  | Hose Reels | Hose Reel Cabinets | Cabinet | Linked Child |  |  |  | Hose Reel Assembly | Choice
4 |  | Hose Reels | Hose Reel Valves | Valve | Linked Child |  |  |  | Hose Reel Assembly | Choice
5 | Means of Restricting Fire Spread / Structural Protection | Wall Assemblies | Plasterboard Wall Assembly | Plasterboard Wall Assembly | Input |  |  | m2 | [6 empty] | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied.
5 |  | Wall Assemblies | Speed Panel Wall Assembly | Speed Panel Wall Assembly | Input |  |  | m2 | [6 empty] | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied.
5 |  | Wall Assemblies | Masonry Wall Assembly | Masonry Wall Assembly | Input |  |  | m2 | [6 empty] | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied.
5 |  | Wall Assemblies | Concrete Wall Assembly | Concrete Wall Assembly | Input |  |  | m2 | [6 empty] | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied.
5 |  | Wall Assemblies | Fire Batts | Mastic Fire batt | Input |  |  | kg
5 |  | Doors and Glazing | Fire Doors | Fire Door | Input |  |  | doors
5 |  | Doors and Glazing | Smoke Doors | Smoke Door | Input |  |  | doors
5 |  | Doors and Glazing | Non-Fire-Rated Doors | Non-Fire-Rated Door | Input |  |  | doors
5 |  | Doors and Glazing | Fire Resistant Glazing | Glass Glazing | Input |  |  | kg
5 |  | Doors and Glazing | Heat Strengthened Glazing | Heat Strengthened Glazing | Input |  |  | m2
5 |  | Pipework Protection | Intumescent Collars | Fire collar | Input |  |  | kg | [6 empty] | Ensure the selected product's size is suitable for the actual pipe diameter being protected.
5 |  | Pipework Protection | Fire-Resistant Joint Seals | Fire-Resistant Joint Seal | Input |  |  | seals | [6 empty] | Ensure the selected product's size is suitable for the actual joint/pipe size being protected.
5 |  | Pipework Protection | Intumescent Pipe Wraps | Intumescent Pipe Wrap | Input |  |  | m | [6 empty] | Ensure the selected product's size is suitable for the actual pipe diameter being wrapped.
5 |  |  | Fire-Resistant Mastic | Fire-Resistant Mastic | Input |  |  | kg,L
5 |  |  | Fire-Stop Mortar | Fire-Stop Mortar | Input |  |  | kg,L
5 |  |  | Applied Structural Fire Protection | Applied Structural Fire Protection | Input |  |  | m2
5 |  |  | Fire Shutters | Fire Shutter | Input |  |  | unit
5 |  |  | Fire Curtains | Fire Curtain | Input |  |  | m2
6 | Means of Suppression | Sprinklers | Sprinkler Heads | Sprinkler Head | Input | Total Quantity,Grid Spacing,Coverage Area | Y
6 |  | Sprinklers | Sprinkler Pipework | Sprinkler Pipework | Input | Total Quantity,Formula |  |  | Sprinkler Heads |  | sprinkler | pipework | vertical_riser_formula,horizontal_pipe_formula |  | The Formula option is an early-stage geometric approximation, not a cited AS clause - verify before relying on it for design.
6 |  | Sprinklers | Sprinkler Valves | Sprinkler Valve | Linked Child |  |  |  | Sprinkler Heads | Choice
6 |  | Sprinklers | Sprinkler Pumps | Sprinkler Pump | Input |  |  | pumps
6 |  | Hydrants | Hydrant Valves | Hydrant Valve | Input |  |  | valves | [6 empty] | A reference formula exists in calc_rules (Risers x Storeys x Outlets per Riser per Storey) - it's a simplified proxy, not a direct AS2419.1 quantity rule. Confirm the required quantity manually.
6 |  | Hydrants | Hydrant Pipework | Hydrant Pipework | Input |  |  | m
6 |  | Hydrants | Hydrant Boosters | Hydrant Booster | Input |  |  | boosters | [6 empty] | Typically 1 booster assembly per hydrant system - confirm against site layout and AS2419.1.
6 |  | Hydrants | Hydrant Pumps | Hydrant Pump | Input |  |  | pumps
7 | Means of Smoke Hazard Management |  | Smoke Exhaust Fans | Smoke Exhaust Fan | Input |  |  | fans
7 |  |  | Fire Resistant Ductwork | Fire Resistant Ductwork | Input |  |  | m | [6 empty] | Ensure the selected product matches the desired duct size.
7 |  |  | Regular Sheet Metal Ductwork | Regular Sheet Metal Ductwork | Input |  |  | m | [6 empty] | Ensure the selected product matches the desired duct size.
8 | Means of Fire Brigade Access and Intervention |  | Fire Control Centre | Fire Control Centre | Input |  |  | centres
9 | Fire Safety Management |  | Fire Safety Signage | Fire Safety Signage | Input |  |  | signs
9 |  |  | Evacuation Diagram Systems | Evacuation Diagram System | Input |  |  | systems
9 |  |  | Fire Equipment Identification Signs | Fire Equipment Identification Sign | Cross-Category Counter | [8 empty] | Portable Extinguishers,Hose Reel Assembly,Hydrant Valves,Hydrant Boosters
3 | Means of Egress |  | Emergency Luminaires | Emergency Luminaire | Input | Total Quantity,Grid Spacing,Coverage Area
3 |  |  | Illuminated Exit Signs | Illuminated Exit Sign | Input | Total Quantity |  | signs
3 |  |  | Directional Exit Signs | Directional Exit Sign | Input | Total Quantity |  | signs
10 | Special Hazards |  | Data-Centre Gaseous Suppression Systems |  | Unavailable
10 |  |  | Battery Energy Storage Fire Protection Systems |  | Unavailable
10 |  |  | Commercial Kitchen Suppression Systems |  | Unavailable
10 |  |  | Carpark Special Detection Systems |  | Unavailable
10 |  |  | Atrium Fire and Smoke-Control Systems |  | Unavailable
5 |  |  | Motorized Fire/Smoke Dampers | Motorized Dampers | Input |  |  | kg | [6 empty] | Ensure the selected product's size is suitable for the actual duct size being protected.
5 |  |  | Fusible Link Fire/Smoke Dampers | Fusible link damper | Input |  |  | kg | [6 empty] | Ensure the selected product's size is suitable for the actual duct size being protected.
5 |  | Doors and Glazing | Fire Doors (Steel with Glazing) | Fire Door(Steel with Glazing) | Input |  |  | m2