## ui_structure
Category | Category Name | System | Apparatus | Product Type | Formula | ID_Linked_to_EC_Database | Archetype | Modes | Disclaimer | Info | Quantity Unit | Requires FRL
1 | Means of Detection | Fire Detection and Alarm System | Smoke Detectors | point-type smoke detector, point-type smoke detector with sounder | ROUNDUP(number_of_storey * floor_area_per_storey / smoke_detector_coverage_area) | Smoke Detector | Input | Coverage Area,Grid Spacing |  | NCC Specification 20 (S20C2–S20C8) / E2D3–E2D20 (class-specific) / AS 1670.1 | units
1 | Means of Detection | Fire Detection and Alarm System | Heat Detectors | heat detector, heat detector with sounder | ROUNDUP(number_of_storey * floor_area_per_storey / heat_detector_coverage_area) | Heat Detector | Input | Coverage Area,Grid Spacing |  | AS1670.1 | units
1 | Means of Detection | Fire Detection and Alarm System | Manual Call Points |  | ROUNDUP(number_of_storey * fire_stairs_per_stoery) | Manual Call Point | Input |  |  |  | units
1 | Means of Detection | Fire Detection and Alarm System | Fire Indicator Panels |  | 1 | Fire Indicator Panel | Input |  |  | A building or campus will typically have a main FIP. Depending on the project size and fire alarm zoning requirements, sub-FIPs should be considered. | units
1 | Means of Detection | Fire Detection and Alarm System | Fire Detection Cabling |  |  | Fire Detection Cabling | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Input/Output Module |  |  | Input/Output Module | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | End-of-Line Device |  |  | End-of-Line Device | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Mimic Panel |  |  | Mimic Panel | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Fire Detection and Alarm System | Graphic Display Panel |  |  | Graphic Display Panel | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detectors |  | ROUNDUP(number_of_storey * floor_area_per_storey / aspirating_detector_coverage_area) | Aspirating Unit | Input | Coverage Area,Grid Spacing |  |  | units
1 | Means of Detection | Aspirating Smoke Detection System | Aspirating Detector Pipework |  |  | Sampling Pipework | Input |  |  |  | kg
1 | Means of Detection | Special Detection System | CO Detector |  |  | Unavailable | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
1 | Means of Detection | Special Detection System | Flame Detector |  |  | Unavailable | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
1 | Means of Detection | Special Detection System | Combination CO/Flame Detector |  |  | Unavailable | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
1 | Means of Detection | Special Detection System | Lithium-Ion Battery Detector |  |  | Unavailable | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | EWIS Panels |  | 1 | EWIS panel | Input |  |  | A building or campus will typically have a main EWIS. Depending on the project size and fire alarm zoning requirements, sub-EWIS should be considered. | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Speakers | Standard Speaker, Horn Speaker | ROUNDUP(MAX (room_number, number_of_storey * floor_area_per_storey / speaker_coverage_area)) | Speaker | Input | Coverage Area,Grid Spacing |  | Speaker types may vary depending on the acoustic and operational requirements of the area. Speaker spacing is generally determined by the selected manufacturer's requirements and may vary depending on the speaker type and ceiling height. For preliminary planning purposes, the spacing between adjacent speakers has been estimated at approximately two times the ceiling height or spaced as 7m X 7m, subject to confirmation against the selected manufacturer's design criteria and acoustic performance requirements. Each room would require a speaker at least. | units
2 | Means of Warning | EWIS / Voice Alarm and Intercom System | Warden Intercom Point |  |  | Unavailable | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
2 | Means of Warning | Visual Warning System | Visual Alarm Devices |  | ROUNDUP(room_number, number_of_storey * floor_area_per_storey / VAD_coverage_area) | Visual alarm device | Input | Coverage Area,Grid Spacing |  | Spacing based on manufacturer requirements, but is only required in areas where speech intelligibility is not achieved. Normally spaced as 7m X 7m. | units
2 | Means of Warning | Audible Warning System | Sounders |  | ROUNDUP(MAX (room_number, number_of_storey * floor_area_per_storey / sounder_coverage_area)) | Unavailable | Unavailable | Coverage Area,Grid Spacing | Future Implmentation: Embodied carbon data is not currently available. | Spacing is dependent on manufacturer's requirement, normally spaced as 10m X 10m. | units
2 | Means of Warning | Fire Alarm Cabling | EWIS Fire-Rated Cabling |  |  | Unavailable | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | m
3 | Means of Egress | Emergency Lighting System | Emergency Luminaires |  |  | Emergency Luminaire | Input | Coverage Area,Grid Spacing |  | NCC E4D2 / E4D3 / AS/NZS 2293.1 | units
3 | Means of Egress | Exit Signage System | Exit Signs | Illuminated Exit Sign, Directional Exit Sign | ROUNDUP(number_of_storey * fire_stairs_per_stoery) | Illuminated Exit Sign | Input |  |  | NCC E4D5 / E4D6 / Specification 25 / AS/NZS 2293.1 | units
4 | Means of First Aid Fire-Fighting | Portable Extinguisher System | Extinguishers | CO₂, Dry Powder, Water, Wet Chemical | number_of_storey * ROUNDUP(floor_area_per_storey / extinguisher_coverage_area) | Extinguishers | Input |  |  | NCC E1D14 / E1P1 / AS 2444 | units
4 | Means of First Aid Fire-Fighting | Fire Blanket | Fire Blanket | 0.9m X 0.9m, 1.8m X 1.8m |  | Fire Blanket | Unavailable |  |  | AS 2444 - 2001
4 | Means of First Aid Fire-Fighting | Fire Hose Reels | Hose Reel Assembly | 19 mm hose reel, 25 mm hose reel | ROUNDUP(number_of_storey * fire_stairs_per_stoery) | Hose Reel Assembly | Input |  |  | NCC E1D3(2) / E1D3(1)(a) exemption Cl 2,3,5 / AS 1221 | reels
4 | Means of First Aid Fire-Fighting | Fire Hose Reels | Hose Reel Pipework | Copper, Galvanised mild steel, HDPE |  | Pipework | Unavailable |  |  | Hose reel pipework shall comply with AS 2419.1 or AS 2118.1 or AS 3500.1, subject to the system configuration and applicable requirements. Pipe material selection may also vary between above ground and below ground applications. In Sydney, most of projects use copper since hose reel water comes from cold water system. | m
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Plasterboard Wall Assembly |  |  | Fire Resistant Plasterboard | Input |  | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  | m2 | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Speed Panel Wall Assembly |  |  | Speed Panel | Input |  | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  | m2 | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Masonry Wall Assembly |  |  | Masonry | Input |  | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  | m2 | Y
5 | Means of Restricting Fire Spread / Structural Protection | Fire-Rated Wall Assemblies | Concrete Wall Assembly |  |  | Concrete | Input |  | Required FRL is a direct user override (no NCC lookup is performed) - select the Product Type matching the required FRL and construction thickness. Carbon factors assume a standard reference density to convert the manufacturer's per-kg factor to a per-m² wall rate, since no project-specific density was supplied. |  | m2 | Y
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors |  |  | Fire Door | Input |  |  | NCC C4D2–C4D8 (class-specific) / Specification 12 / AS 1905.1 | units
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Doors (Steel with Glazing) |  |  | Fire Door(Steel with Glazing) | Input |  |  | NCC C4D2–C4D8 (class-specific) / Specification 12 / AS 1905.2 | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Resistant Glazing |  |  | Glass Glazing | Input |  |  | NCC C4D2 / AS 1288 / Specification 35 | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Smoke Doors |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | doors
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Shutters |  |  | Fire Shutter | Input |  |  | NCC C4D2 / AS 1905.2 (openings requiring FRL) | m2
5 | Means of Restricting Fire Spread / Structural Protection | Opening Protection | Fire Curtains |  |  | Fire Curtain | Input |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Duct Penetration Protection | Fusible-Link Fire Damper |  |  | Fusible link damper | Input |  | Ensure the selected product's size is suitable for the actual duct size being protected. | NCC E2D4–E2D13 / Specification 11 / C4D15 (at fire barrier penetrations) | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire Batts |  |  | Mastic Fire batt | Input |  |  |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Collars |  |  | Fire collar | Input |  | Ensure the selected product's size is suitable for the actual pipe diameter being protected. |  | units
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Joint Seals |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Intumescent Pipe Wraps |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | m
5 | Means of Restricting Fire Spread / Structural Protection | Penetration and Joint Fire-Stopping | Fire-Resistant Mastic |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | kg
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Intumescent Coating |  |  | Intumescent coating | Input |  |  |  | m2
5 | Means of Restricting Fire Spread / Structural Protection | Structural Fire Protection | Spray-Applied Fire Protection |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | m2
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Heads | Exposed, Concealed, Semi-Recessed, Sidewall | ROUNDUP(number_of_storey * floor_area_per_storey / sprinkler_coverage_area) | Sprinkler Heads | Input | Coverage Area,Grid Spacing |  | NCC Part E1 Specification 17 / AS 2118.1 hazard-based spacing | units
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Pipework | galvanised mild steel |  | Sprinkler Pipework | Input |  |  | NCC Part E1 Specification 17 / Refer to AS 2118.1:2017 Clause 7.10 for sprinkler pipework material requirements | m
6 | Means of Suppression | Wet Pipe Sprinkler System | Sprinkler Valves |  |  | Sprinkler Valves | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Sprinkler Heads |  |  | Pre-Action Sprinkler Heads | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Dry Pipework | hot-dip galvanised medium steel tube |  | Dry Pipework | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. | Refer to AS 2118.1:2017 Clause 7.10 for sprinkler pipework material requirements | m
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Pre-Action Valve Assembly |  |  | Pre-Action Valve Assembly | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
6 | Means of Suppression | Dry Pre-Action Sprinkler System | Nitrogen Generator |  |  | Nitrogen Generator | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | units
6 | Means of Suppression | Fire Water Supply Equipment | Main Fire Pump Set | Electric-Driven, Diesel-Driven | IF(effective_height > 25, 1 , 0) | Main Fire Pump Set | Input |  |  | Pump duty requirements vary depending on building height, building classification, system demand and whether the installation serves a dedicated fire hydrant and sprinkler system. | kg
6 | Means of Suppression | Fire Water Supply Equipment | Jockey Pump Set |  | IF(effective_height > 25, 1 , 0) | Jockey Pump Set | Input
6 | Means of Suppression | Fire Water Supply Equipment | Water Tank | Reinforced Concrete, Stainless Steel |  | Water Tank | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. | Tank capacities vary depending on building height, building classification and system configuration.
6 | Means of Suppression | Fire Water Supply Equipment | Sprinkler Booster Assembly |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Exhaust Fan |  |  | Smoke Exhaust Fan (notional - 1000mm) | Input |  |  |  | kg
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Smoke Subducts | Fire-Rated, Non-Fire-Rated |  | Smoke Subducts | Input |  | Ensure the selected product matches the desired duct size. |  | m2
7 | Means of Smoke Hazard Management | Mechanical Smoke Control System | Motorised Smoke Dampers |  |  | Motorised Smoke Dampers | Input |  | Ensure the selected product's size is suitable for the actual duct size being protected. |  | units
8 | Means of Fire Brigade Access and Intervention | Hydrant System | Hydrants |  | ROUNDUP(number_of_storey * fire_stairs_per_stoery) | Hydrants | Input |  | Each fire isolated stair will typically require a fire hydrant. Where the required hydrant coverage cannot be achieved from these hydrants alone, additional internal hydrants may be required. | Refer to NCC Part E1P3
8 | Means of Fire Brigade Access and Intervention | Hydrant System | Hydrant Pipework |  |  | Hydrant Pipework | Input |  |  | Refer to NCC Part E1P3 Refer to AS 2419.1:2021 Clause 9.2 for fire hydrant pipework material requirements. Typically utilis galvanized mild steel medium and hot dipped galvanised steel. | m
8 | Means of Fire Brigade Access and Intervention | Hydrant System | Hydrant Booster Assembly |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. | Refer to NCC Part E1P3
9 | Fire Safety Management | Fire Safety Signage and Information | Regulatory and Operational Signs |  |  | Fire Safety Signage System | Input |  |  |  | units
9 | Fire Safety Management | Fire Safety Signage and Information | Evacuation Diagrams | Standard Evacuation Diagram |  | Evacuation Diagram System | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available. |  | systems
9 | Fire Safety Management | Fire Safety Signage and Information | Fire Equipment Identification Signs | Extinguisher, Hose Reel, Hydrant |  | Fire Equipment Identification Sign | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
10 | Special Hazards | Special Hazard Systems | Data-Centre Gaseous Suppression Systems |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
10 | Special Hazards | Special Hazard Systems | Battery Energy Storage Fire Protection Systems |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
10 | Special Hazards | Special Hazard Systems | Commercial Kitchen Suppression Systems |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
10 | Special Hazards | Special Hazard Systems | Carpark Special Detection Systems |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.
10 | Special Hazards | Special Hazard Systems | Atrium Fire and Smoke-Control Systems |  |  |  | Unavailable |  | Future Implmentation: Embodied carbon data is not currently available.

## Condition
Parameter | Condition Key 1 | Condition Value 1 | Condition Key 2 | Condition Value 2 | Condition Key 3 | Condition Value 3 | value | unit | note
smoke_detector_coverage_area | default | default | default | default | default | default | 104.04 | m2 | AS1670.1 10.2m x 10.2m coverage
heat_detector_coverage_area | default | default | default | default | default | default | 51.84 | m2 | AS1670.1 7.2m x 7.2m coverage
aspirating_detector_coverage_area | default | default | default | default | default | default | 250 | m2
speaker_coverage_area | default | default | default | default | default | default | 49 | m2
VAD_coverage_area | default | default | default | default | default | default | 49 | m2
sounder_coverage_area | default | default | default | default | default | default | 100 | m2
sprinkler_coverage_area | fire_hazard | High Hazard | default | default | default | default | 9 | m2 | AS 2118.1 hazard-based spacing
sprinkler_coverage_area | fire_hazard | Ordinary Hazard | default | default | default | default | 12 | m2 | AS 2118.1 hazard-based spacing
sprinkler_coverage_area | fire_hazard | Light Hazard | default | default | default | default | 21 | m2 | AS 2118.1 hazard-based spacing
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 1A | 100 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 2A | 300 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 3A | 450 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 4A | 675 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 5B | 15 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 10B | 45 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 20B | 80 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 2A | 100 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 3A | 300 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 4A | 450 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 6A | 675 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 20B | 80 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 30B | 115 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 40B | 150 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 2A | 150 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 3A | 200 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 4A | 300 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 6A | 450 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 10A | 675 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 40B | 150 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 60B | 225 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | no | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 80B | 300 | m2 | AS 2444 Table 4.2
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 1A | 150 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 2A | 450 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 3A | 675 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 4A | 1000 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 5B | 80 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 10B | 115 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Light Hazard | Minimum_rating_and_classification_of_extinguisher | 20B | 150 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 2A | 150 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 3A | 450 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 4A | 675 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 6A | 1000 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 20B | 150 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 30B | 225 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | Ordinary Hazard | Minimum_rating_and_classification_of_extinguisher | 40B | 300 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 2A | 225 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 3A | 300 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 4A | 450 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 6A | 675 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 10A | 1000 | m2 | AS 2444 Table 4.1
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 40B | 150 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 60B | 225 | m2 | AS 2444 Table 4.3
extinguisher_coverage_area | automatic_fixed_suppression | yes | fire_hazard | High Hazard | Minimum_rating_and_classification_of_extinguisher | 80B | 300 | m2 | AS 2444 Table 4.3

## frl_reference
Apparatus | Product Type | FRL (min) | Thickness (mm) | Layers | Density (kg/m3)
Concrete | 20MPa | 30 | 60 |  | 2400
Concrete | 20MPa | 60 | 80 |  | 2400
Concrete | 20MPa | 90 | 100 |  | 2400
Concrete | 20MPa | 120 | 120 |  | 2400
Concrete | 20MPa | 180 | 150 |  | 2400
Concrete | 20MPa | 240 | 175 |  | 2400
Masonry |  | 30 | 60 |  | 1900
Masonry |  | 60 | 90 |  | 1900
Masonry |  | 90 | 110 |  | 1900
Masonry |  | 120 | 130 |  | 1900
Masonry |  | 180 | 160 |  | 1900
Masonry |  | 240 | 180 |  | 1900
Speed Panel |  | 60 | 51 |  | 600
Speed Panel |  | 90 | 64 |  | 600
Speed Panel |  | 120 | 78 |  | 600
Fire Resistant Plasterboard |  | 30 | 13 | 2
Fire Resistant Plasterboard |  | 60 | 16 | 1
Fire Resistant Plasterboard |  | 90 | 13 | 2
Fire Resistant Plasterboard |  | 120 | 16 | 2