## Building Class
Building class | Sprinkler systems | Fire hydrant systems | Fire hose reels | Portable fire extinguishers | Fire detection systems | Alarm / warning systems | Emergency lighting | Exit signs / direction signs | Smoke exhaust fans | Stair pressurization | Smoke dampers | Smoke ductwork | Fire doors | Smoke doors | Door Closers | Door seals | Sealants
2 (Apartments) | Yes | yes | No | yes | yes | yes | yes | yes | No - exempt | Conditional - Mandatory if effective height >25m E2D4 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D3 | No | Conditional - Mandatory for all openings required to have FRL
3 (hotels/hostels) | yes | yes | No | yes | yes | yes | yes | yes | No - exempt | Conditional - Mandatory if effective height >25m E2D5 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D4 | No
5 (offices) | yes | yes | No | yes | yes | conditional (if building requires) | yes | yes | Conditional - Mandatory if effective height >25m AND >18,000 m² floor area or >108,000 m³ volume (E1D10) | Conditional - Mandatory if effective height >25m E2D6 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D5 | Conditional - Required only where active exhaust installed.
6 (retail) | conditional (if floor area > 3500m2, volume > 21000m3) | yes | yes | yes | yes | yes | yes | yes | Conditional - E2D14/E2D15: additional requirements apply to Cl 6 fire compartments >2,000 m². | Conditional - Mandatory if effective height >25m E2D7 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D6 | Conditional - Required only where active exhaust installed.
7 (carparks/storage) | conditional (if a separated building) | yes | yes | yes | yes | conditional (if building requires) | yes | yes |  | Conditional - Mandatory if effective height >25m E2D8 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D7 | Conditional - Required only where active exhaust installed.
8 (electricity network) | conditional (if floor area > 200m2) | conditional (if can be connected to town main supply) | No | yes | yes | conditional (if building requires) | yes | yes |  | Conditional - Mandatory if effective height >25m E2D9 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D8 | Conditional - Required only where active exhaust installed.
9a (healthcare) | yes | yes | yes | yes | yes | yes | yes | yes | Conditional - E2D11: smoke detection + HVAC shutdown required if rise in storeys >2, E1D10 applies also | Conditional - Mandatory if effective height >25m E2D10 | Yes | Conditional - Required only where active exhaust installed.
9b (early childhood centre) | conditional (if rise in storeys <2) | yes | yes | yes | yes | yes | yes | yes |  | Conditional - Mandatory if effective height >25m E2D11 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D10 | Conditional - Required only where active exhaust installed.
9c (aged care) | yes | yes | No | yes | yes | yes | yes | yes | Conditional - (E1D10) | Conditional - Mandatory if effective height >25m E2D12 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D11 | Conditional - Required only where active exhaust installed.
Reference | NCC E1D4 | NCC E1D2 | NCC E1D3 | NCC E1D14 | NCC S31C15 | NCC S31C18/ AS1670.1 | NCC E4V1 | NCC E4D5/ E4D6