## Standards List
System | Components | Required | Conditional type | condition value | Reference
Sprinkler systems | Sprinkler heads | Yes | Always | - | NCC Part E1 / Specification 17
Sprinkler systems | sprinkler pipework | yes | Always | - | NCC Part E1 / Specification 17
Sprinkler systems | control valves | yes | Always | - | NCC Part E1 / Specification 17
Sprinkler systems | pumps | yes | building height > | 25 m | NCC Part E1 / Specification 17
Sprinkler systems | water tanks | yes | town water | No | NCC Part E1 / Specification 17
Sprinkler systems | booster connection | Yes | Always | - | NCC Part E1 / Specification 17
Fire hydrant systems | Hydrant valves | Yes | Always | - | NCC Part E1
Fire hydrant systems | hydrant pipework | yes | Always | - | NCC Part E1
Fire hydrant systems | booster assembly | yes | Always | - | NCC Part E1
Fire hydrant systems | pumps | yes | building height > | 50 m | NCC Part E1
Fire hydrant systems | water tanks | yes | town water | No | NCC Part E1
Fire hose reels | Hose reels | yes | Always | - | NCC Part E1
Fire hose reels | cabinets | yes | Always |  | NCC Part E1
Fire hose reels | pipework | yes | Always |  | NCC Part E1
Portable fire extinguishers | Extinguishers | yes | always |  | NCC Part E1
Portable fire extinguishers | brackets | yes | cabinet | yes | NCC Part E1
Portable fire extinguishers | cabinets | yes | weather protection | yes | NCC Part E1
Fire detection systems | Smoke detectors | yes | always |  | NCC Part E2 / Specification 20
Alarm / warning systems | Fire indicator panel | yes | always |  | NCC Part E4 / Specification 20
Alarm / warning systems | sounder | yes | building class | based on NCC/AS 1670.1
Alarm / warning systems | strobes | yes | hearing-imparied occupants | yes
Alarm / warning systems | speakers | yes | building height/ NCC | EWIS present
Alarm / warning systems | EWIS | yes | effective height > | 25 m
Alarm / warning systems | manual call points | yes | fire detection system exits in building | yes
Alarm / warning systems | cabling | yes | Always
Emergency lighting | Emergency luminaires | yes | Always |  | NCC Part E4
Emergency lighting | exit luminaires | yes | exit sign installed | yes
Emergency lighting | central battery system | yes | battery type | central battery
Emergency lighting | local battery packs | yes | battery type | self-contained
Emergency lighting | emergency lighting cabling | yes | Always
Exit signs / direction signs | Exit signs | yes | exit required | yes | NCC Part E4 / Specification 25
Exit signs / direction signs | direction signs | yes | exit not immediately visible | yes
Exit signs / direction signs | photoluminescent exit signs | yes | electrical supply not required | yes
Exit signs / direction signs | mounting brackets/fixings | yes | Always
Smoke Hazard management | Smoke exhaust fans | yes | Floor Area> | 2000m2 | NCC part E2 / E2D2
Smoke Hazard management | Stair Pressurization | yes | Effective height> | 25 m | NCC part E2 / AS 1668.1
Smoke Hazard management | Smoke Dampers | yes | Ductwork | If duct penetrates through fire proof wall | NCC part C / specification 11, NCC part E2
Smoke Hazard management | Ductwork | yes | Smoke exhaust/stair pressurization | yes | NCC Part E2 / Specification 21
Smoke Hazard management | control cabling | yes | Always
Smoke and heat vents | roof vents | yes | Always |  | NCC Part E2 / Specification 22
Smoke and heat vents | control cabling | yes | Always |  | NCC Part E2 / Specification 22/ AS 2665
Smoke and heat vents | Vent actuators | yes | automatic vent installed | yes | NCC Part E2 / Specification 22
Fire doors / smoke doors | Fire doors | yes | FRL required | yes | NCC part C4 / C4D2
Fire doors / smoke doors | Smoke doors | yes | Smoke compartments needed | yes | NCC part C4 / C4/D3
Fire doors / smoke doors | Closers | yes | Fire doors/smoke doors used | yes | NCC specification 12
Fire doors / smoke doors | Seals | yes | Smoke doors used | yes | NCC S12C4
Fire doors / smoke doors | Hold open devices | no
Fire shutters/ fire windows | Fire shutters | yes
Fire shutters/ fire windows | fire-rated glazing | yes
Fire shutters/ fire windows | fire windows | yes | fire-rated glazing installed | yes
Fire stopping/penetration seals | Fire collars | no
Fire stopping/penetration seals | sealants | yes | ductwork penetrates through fireproof element | yes
Fire stopping/penetration seals | fire pillows | no
Fire stopping/penetration seals | cable/pipe penetration systems | no

## Building Class
Building class | Sprinkler systems | Fire hydrant systems | Fire hose reels | Portable fire extinguishers | Fire detection systems | Alarm / warning systems | Emergency lighting | Exit signs / direction signs | Smoke exhaust fans | Stair pressurization | Smoke dampers | Smoke ductwork | Fire doors | Smoke doors | Door Closers | Door seals | Sealants
2 (Apartments) | Yes | yes | No | yes | yes | yes | yes | yes | No - exempt | Conditional - Mandatory if effective height >25m E2D4 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D3 | No | Conditional - Mandatory for all openings required to have FRL
3 (hotels/hostels) | yes | yes | No | yes | yes | yes | yes | yes | No - exempt | Conditional - Mandatory if effective height >25m E2D5 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D4 | No
5 (offices) | yes | yes | No | yes | yes | conditional (if building requires) | yes | yes | Conditional - Mandatory if effective height >25m AND >18,000 m² floor area or >108,000 m³ volume (E1D10) | Conditional - Mandatory if effective height >25m E2D6 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D5 | Conditional - Required only where active exhaust installed.
6 (retail) | conditional (if floor area > 3500m2, volume > 21000m3) | yes | yes | yes | yes | yes | yes | yes | Conditional - E2D14/E2D15: additional requirements apply to Cl 6 fire compartments >2,000 m². | Conditional - Mandatory if effective height >25m E2D7 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D6 | Conditional - Required only where active exhaust installed.
7 (carparks/storage) | conditional (if a separated building) | yes | yes | yes | yes | conditional (if building requires) | yes | yes |  | Conditional - Mandatory if effective height >25m E2D8 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D7 | Conditional - Required only where active exhaust installed.
8 (electricity network) | conditional (if floor area > 200m2) | conditional (if can be connected to town main supply) | No | yes | yes | conditional (if building requires) | yes | yes |  | Conditional - Mandatory if effective height >25m E2D9 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D8 | Conditional - Required only where active exhaust installed.
9a (healthcare) | yes | yes | yes | yes | yes | yes | yes | yes | Conditional - E2D11: smoke detection + HVAC shutdown required if rise in storeys >2, E1D10 applies also | Conditional - Mandatory if effective height >25m E2D10 | Yes | Conditional - Required only where active exhaust installed.
9b (early childhood centre) | conditional (if rise in storeys <2) | yes | yes | yes | yes | yes | yes | yes |  | Conditional - Mandatory if effective height >25m E2D11 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D10 | Conditional - Required only where active exhaust installed.
9c (aged care) | yes | yes | No | yes | yes | yes | yes | yes | Conditional - (E1D10) | Conditional - Mandatory if effective height >25m E2D12 | Conditional - required whenever HVAC ducts penetrate fire barriers E2D11 | Conditional - Required only where active exhaust installed.
Reference | NCC E1D4 | NCC E1D2 | NCC E1D3 | NCC E1D14 | NCC S31C15 | NCC S31C18/ AS1670.1 | NCC E4V1 | NCC E4D5/ E4D6